## HOTO Version Log
HOTO Version Control | Date Issued | Previous Item | Updated Item | Comments/Notes | Impact | Comments
v6.2 | 2021-01-15 | 1.2 | 2.6 | SSB requirement moved from Project Planning to Project Design to align with SSB Instructions on DEQMS | Nil
|  | 1.3 | 1.2 | Building Contribution Factor for Existing Facilities renumbered to accommodate removal of item 1.3 | Nil
|  | 2.6 | 2.7 | Property Licence requirement renumbered to accommodate for inclusion of SSB Item 2.6 | Nil
|  |  | 5.8.8 | 2. Radiation Safety Considerations included in Handover / Takeover | New
v6.3 | 2021-02-25 | 5.1 | 5.1 | Notice of Completion - item removed | Removed
v7.0 | 2021-07-01 | v6.3 | v7.0 | HOTO Criteria removed or consolidated and inclusion of Data Provision Checklist (DPC) | Nil
| 2022-05-03 | V7 | v7.1 | Minor update to paragraph 7 of the HOTO instruction and inclusion of EIPP Template. | Nil
| 2023-02-08 | v7.1 | v7.2 | Update Links/emails, Introduce Assurance and Validation checklist Requirement & AUC update | Nil
| 2023-07-28 | v7.2 | v7.3 | DEQMS to ERIK update & incorporation Of EGIS updates | Nil
| 2024-11-03 | v7.3 | v7.4 | Minor update: Maintenance Agent & Asset Rollout Notification separated into 3 Steps. | Nil
| 2025-08-14 | 7.4 | v7.5 | DPC items 3,9,10,12,16 (criteria) & 20 (description) updated to align with EDGA process. Asset Rollout description updated 3.5,5.35,6.4. 5. & item 5.18 Classification updated per DSPF. ERIK to Defence Intranet update. | Nil
| 2026-02-25 | 7.5 | 7.6 | EMOS references updated to PAS, include PAS Data Service. Project Source Formatting

## HOTO Instructions
HANDOVER / TAKEOVER INSTRUCTIONS
HOTO Version 7.6 Updated 25 Feb 2026 Sponsor: DG ESD & DG CFI Administrator: DELM Contact: segservicedelivery.esddelm@defence.gov.au
Introduction
1. The handover (HO) of a project by the contractor (Head Contractor [HC]) to the Commonwealth (i.e. appointed Representative and/or Project Manager (PM)) and takeover (TO) of a project deliverables by the Defence Representative at the end of the delivery phase are very important stages of the project procurement process, ensuring that a fit for purpose and safe for use asset is delivered. A well organised, efficient and effective transfer of the assets (including leased property) and complete and accurate estate information from the project to Defence is essential to ensure Defence assets are operated and maintained safely, efficiently and in compliance with all applicable legislation, Defence policy and Australian Standards.
2. To minimise issues during a project’s planning, design, delivery & defect liability period (DLP) phases and to streamline the Handover / Takeover (HOTO) process; it is essential that all Defence estate projects satisfy and complete a range of legislative, Defence policy, estate compliance and estate information requirements during these phases. Ensuring compliance with these Defence requirements is achieved by understanding roles and responsibilities, early planning and engagement, ongoing consultation, use of the Defence HOTO Plan and Checklist to plan, implement and assure critical HOTO related activities throughout the project lifecycle. Further information about HOTO stakeholder roles can be found in the HOTO - Responsible, Accountable, Consulted, Informed (RACI) Workbook.
3. The HOTO documents contained within this workbook detail the actions and evidence required by Defence to demonstrate that the delivered project works and activities are completed, accurately recorded, suitable for use and occupancy by Defence. The Project Lifecycle & HOTO Plan and Project Lifecycle Criteria Instructions will assist project stakeholders in developing project and assurance plans for the provision of project deliverables and required actions throughout the project lifecycle. By planning, monitoring, completing and assuring the agreed criteria in project planning, design and construction phases; greater success and timeliness can be achieved for HOTO and DLP.
Aim
4. The aim of the HOTO instructions is to direct key project stakeholders in development and management of Project HOTO Plan and Checklist and collating the evidentiary requirements pertaining to project specific and mandatory legislative deliverables.
HOTO Policy
5. The Defence HOTO policy applies to all Defence estate projects. The policy can be found on Defence Intranet at:
https://dpeintranet-seg.defence.gov.au/guidance-compliance/facilities-estate-management/project-program-management/handover-takeover-process
Scope & Application
6. The use of the HOTO Plan and Checklist document and development of a Project Lifecycle & HOTO Plan - 'HOTO plan' and other project plans is to occur for all estate projects involving works on facilities, infrastructure, land, buildings and fixed plant & equipment that result in changes to the Defence estate. Estate projects can include: facilities and infrastructure construction, repurposing, refurbishing, maintenance, facilities works associated with leasing, land acquisition or disposal (including Government Furnished Facilities [GFF] / Government Furnished Equipment [GFE]) and environmental projects delivered by Infrastructure Division (ID) and Service Delivery Division (SDD) and other Groups and Services. Use of the HOTO Plan and checklist is not limited to SEG. Any Defence entity such as Joint Capability Group (JCG) and Capability Acquisition & Sustainment Group (CASG) and their contractors conducting works on facilities must use the HOTO Plan & Checklist to ensure estate compliance and safety outcomes are achieved.
7. The Property and Asset Services (PAS) contractors and PAS PMO must use the HOTO Plan and Checklist in full when delivering SEG Estate Works Program (EWP) allocated maintenance projects. Additionally and as required by their base services contract (BSC), the PAS undertake a range of responsive, scheduled or performance based maintenance on the Defence estate. Substantial maintenance works can also be delivered by the PAS through the Estate Maintenance Request (EMR) process. In both maintenance and EMR instances, PAS use of the HOTO Plan & Checklist during the maintenance activities will assist in identifying changes to estate information and, as required by their contract, managing the currency and accuracy of Defence estate information resulting from their estate maintenance tasks. Use of the HOTO Plan & Checklist and practices by PAS for large / complex maintenance activities, including EMR's, should therefore be part of their internal quality system approach to ensure consistency in the manner in which records are created or updated and contract change proposals (CCP) developed as required. On the basis of this approach, identification and engagement with key stakeholders must continue to occur in these circumstances, however, when completing the HOTO Checklist Signatures tab, stakeholder, Zone Estate Management & Planning (EMP) and Defence representative signatures and approvals is not required.
Authority and Sponsor
8. The HOTO policy is issued under the authority of the First Assistant Secretary, Infrastructure and First Assistant Secretary, Service Delivery. Sponsors of the policy are the Director General Estate Services Delivery and Director General Capital Facilities & Infrastructure (DGCFI). The Directorate Estate & Land Management (DELM) is the administering authority of the HOTO policy which includes ensuring that the policy, HOTO Plan & Checklist and instructions remain current.
Estate Compliance Stakeholders
9. SDD, ID (Environmental & Engineering [EE] Branch), Explosive Ordinance (EO) Branch, Commander Joint Logistics (CJLOG through Fuel Services Branch [FSB]), JCG, Defence Security & Vetting Services (DS&VS) are several key stakeholders that are responsible for defining the applicable compliance requirements and promulgating requirements in Defence policies. Where Defence policies have changed and HOTO details no longer align after the contract award date, the PMCA / PM will liaise with the Commonwealth to determine required actions and instruct the contractor which way to proceed with adjustments (including contract price if determined necessary).
HOTO Terms
10. There are many direct and indirect critical activities exercised throughout the project lifecycle that lead to the principal HOTO activity occurring at the end of the delivery phase. The HOTO event is completed in two stages commencing with the Handover “HO” then followed by the Takeover “TO”. The terms mean:
a. HO. HO is the term used to describe a series of project delivery completion and assurance activities designed to satisfy the Project Manager Contract Administrator (PMCA) / PM that the Contractor has completed all of the required works to a satisfactory standard, the facility is safe and fit for purpose and Defence specified estate information requirements are met (project completion). To the extent that the definition of "Completion" in the relevant project contract refers to the requirements which must be satisfied to achieve "Handover", and this should be read as a reference to achieving "HOTO" under and in accordance with this checklist. The HO is formalised by the contractor providing the required documentary evidence to the PMCA / PM as identified in the HOTO Checklist and HOTO plan and the PMCA / PM notifying acceptance of completion in accordance with the applicable contract clause(s).
b. TO. TO is the term used where the Defence Representative (Zone Director Service Delivery [DSD] or authorised delegate, usually the Zone Assistant Director Estate Management &Planning [AD EMP]) accepts the delivered works from the PMCA / PM into the Defence estate, enabling its use by the resident unit(s) (RU) for its intended purpose and ongoing sustainment by SDD and base services contractors. The acceptance is confirmed by the Defence Representative being satisfied that all project deliverables are satisfactorily completed, the asset(s) is/are fit for purpose, evidentiary and Defence estate information requirements are met (including a list of agreed outstanding items detailed in the HOTO Project Log and Defects list) and signing the completed HOTO Plan & Checklist to that effect.
11. The HOTO checklist introduces terms and a HOTO project log (tab 5) for recording caveats, issues and non-delivered items. The meaning for each of these terms is:
a. Caveat. A caveat is a notice of conditional acceptance of HOTO criteria. For the purpose of Take Over (TO), a caveat will normally be proposed by the PMCA / PM to the Defence Representative (Zone DSD or authorised delegate) for conditional acceptance of HOTO criteria by SDD, where the criteria can be met within an acceptable period of time post HOTO and within the DLP. Caveats will be assessed on their associated risks and must be approved by the Defence Representative to facilitate TO and ongoing facility sustainment.
b. Issue. A matter to be resolved by Defence and the contractor.
c. Incomplete Project Deliverable. A project deliverable not provided by the responsible contracted entity at the required time.
d. Defect. A defect is a fault, imperfection (including shrinkage), deficiency (or omission) in the delivered Works: something not to the required standard. This includes any aspect of the Works which is not in accordance with the requirements of the Works Contract. The defect is to be rectified by the contractor in accordance with the contract and agreed defect rectification plan.
Roles and Responsibilities for HOTO
12. The following roles and responsibilities apply for the HOTO checklist and documents:
a. Defence Representative. The Defence Representative (Zone Director Service Delivery (DSD) or authorised delegate (e.g. Zone AD EMP) is responsible for Takeover (TO) or accepting the delivered works from the Commonwealth Representative (CFI projects - Project Director) and/or PMs, for ongoing sustainment by SDD and Base Services Contractors and enabling its use by the RU for its intended purpose. The acceptance is confirmed by the Defence Representative being satisfied that all project deliverables are satisfactorily completed, are safe and fit for purpose, Defence estate information requirements are met, incomplete or defective works have an acceptable remediation plan and signing the completed HOTO Plan & Checklist to that effect.
b. Zone EMP Representative. The Zone EMP representatives are responsible to contribute to key project activities, identify and raise project issues to the PMCA / PM for resolution and ensure appropriate SDD support is provided throughout the project lifecycle. At HOTO, the Zone EMP representative validates the HOTO Plan & Checklist once completed by the contractor and PMCA / PM and prepares the HOTO submission and recommendation to the Defence Representative.
c. Project Manager Contract Administrator (PMCA) / Project Manager (PM). The PMCA / PM are responsible for managing, assisting and guiding the Contractor with development of the HOTO Plan & Checklist. The PMCA / PM are to ensure that the Contractor has provided all evidence to demonstrate that all project deliverables have been satisfactorily completed, are safe and fit for purpose and the Defence required estate information is accurate and completed. For CFI projects, the PMCA will give directions and carry out all of the other functions under the PMCA services contract and project contract as the agent of the Commonwealth. For EWP projects, the PM role is fulfilled by the Project Delivery Services (PDS) contractor. The PMCA or PM shall not delegate or transfer their HOTO responsibilities to the Property and Asset Services (PAS) contractor.
d. Contractor. The Contractor (can be the Head Contractor, Head Contractor (Medium Works), Managing Contractor and/or Design Services Contractor ) is responsible for conducting all Contractor HOTO obligations within any applicable timeframe prescribed by, or determined in accordance with the HOTO requirements. This includes initiating and ongoing management of the HOTO Plan & Checklist and works are satisfactorily completed, safe, fit for purpose and Defence specified estate information requirements (as detailed on Annexure 1 of the contract) are met.
e. Commonwealth's Representative. The person nominated in the Contract Particulars or any other person nominated by the Commonwealth, For CFI projects this is generally the Project Director (PD) who will give direction to the PMCA.
f. PAS. Throughout the project lifecycle the PAS have two primary roles: to provide advice to the Defence Representative, PMCA / PM and Contractor about Defence estate information and whole of life maintenance requirements. PAS are to ensure that their applicable specialists (subject matter experts [SME]) who understand the project requirements are present at all applicable project meetings, as required.
g. PAS Project Support Service (PSS). PAS PSS staff are the PAS representatives who provide industry expertise and site knowledge to assist projects to maximise the effectiveness of project delivery and achieve project outcomes. PSS will directly provide and/or coordinate the provision of PAS services in support of all CFI and EWP projects.
h. PAS Project Data Service. PAS Data Service staff support all Defence-endorsed projects, including undertaking assurance and validation of new and updated estate data. For Estate Works Program, property acquisition/disposal, and leasing projects, PAS Data Service also manage the collection, creation, and upload of new estate data.
i. Project Stakeholders. Project stakeholders are to attend required project estate planning, design and delivery meetings and contribute to the HOTO process by assisting in the assessment that the facilities are satisfactorily completed, safe and fit for purpose. During the Design phase and at HOTO, all stakeholders (determined at project commencement) are required to sign, acknowledging their acceptance of the scope, design and delivered works.
j. RU. In addition to being stakeholders, RU are not to occupy or use facilities until they have been accepted by the Defence Representative and access granted.
Developing and Completing HOTO Documents
13. The PMCA / PM shall engage with the Zone EMP Representative, PAS PSS and stakeholders at the beginning of the project planning phase to agree initial HOTO requirements prior to engaging the Contractors (HC, MC and / or DSC). The intent of this engagement is to collectively identify and agree on project outcomes, HOTO Checklist, Project Lifecycle & HOTO Plan criteria and evidentiary requirements. Once the Contractor has been engaged, these documents would be reviewed and updated to align with the agreed contract requirements.
14. Defence acknowledges that HOTO documents are updated regularly and projects may have commenced using previous version HOTO documents. Where that has occurred, projects would continue using the HOTO version initiated at contract commencement. However where project stakeholders believe a newer version HOTO Plan & Checklist offer greater benefit to the project, the PMCA / PM can seek approval from the Commonwealth to facilitate a change. The PMCA / PM must consider if a proposed change would adversely impact the contract and/or have a material effect, and present all applicable considerations to the Commonwealth as part of the decision making process.
15. For ease of use, essential HOTO Plan & Checklist documents are collated into an Excel workbook with tabs configured to provide the following information and/or printable documents: a. HOTO Instruction, b. Project Details, c. HOTO Checklist Signatures, d. Project Lifecycle & HOTO Plan, e. Data Provision Checklist, f. DLP Checklist, g. HOTO Caveate Logs, h. Project Lifecycle Criteria Instructions, i. Data Provision Checklist Instructions, h. HOTO RACI, and i. Abbreviations & Definitions.
16. The HOTO Plan & Checklist documents follow a project workflow and summarise actions to ensure that all critical project actions and deliverables leading to HOTO are completed and a record kept by the PMCA / PM, Contractor and PAS PSS to that effect. The Project Lifecycle & HOTO Plan is intended to be used as a detailed "working" document that lists all HOTO criteria and evidence applicable to the project and project lifecycle phase. It is to be regularly reviewed and updated to record HOTO progress throughout each phase. The HOTO checklist signatures provides a high level summary of agreed project HOTO criteria and is used to record the completion of HOTO activities and acceptance by key project stakeholders. PMCA / PM are expected to initially select the applicable HOTO checklist and plan criteria; and details of the evidence to be supplied as part of their project tender submissions. These are later agreed with the Contractor and formalised through the tender and contract negotiation process.
HOTO for Projects with Multiple Delivery Stages and/or Sites.
17. When large and/or complex projects such as a base redevelopment or a large new capability are delivered with multiple distinct delivery stages, a HOTO Plan & Checklist must be developed for each stage. Similarly when CFI or EWP projects are delivering works across multiple Zones, Defence establishments and/or training areas; a HOTO plan & checklist must be used for each location. Where agreed and deemed applicable for delivery at multiple locations (typically for small and simple scope of works), a single HOTO Plan & Checklist can be used. Where possible and after consulting with Zone EMP representatives, this determination is to be made in the planning phase so details can be specified in tender documents by the PMCA / PM . These HOTO arrangements should be further reviewed with the contractor at commencement of the construction phase to ensure the HOTO arrangements (When & number of HOTOs required) are applicable for the project characteristics and schedule.
Project Details
18. The Project Details (tab 0) provides basic list of project details and key stakeholders for the relevant project. The PMCA / PM is to complete as much as possible at the start of the project (i.e. initial project start meeting) and update details as information changes or becomes available.
Project Stakeholders
19. The PMCA / PM and Contractor are responsible for identifying all stakeholders who have an interest in and/or will be a recipient of any of the delivered works under the project. It is important to identify all applicable stakeholders as failure to correctly identify stakeholders could result in works being completed that may not be accepted by the Commonwealth or do not meet the original intent of the project brief.
20. The Contractor and PMCA / PM should liaise with all stakeholders to determine and confirm who needs to provide acceptance of the delivered works, or part thereof. The identified stakeholders must be well prepared and contribute to the successful completion of the HOTO Plan & Checklist. Where projects are delivered across multiple Resident Units (RUs), the PMCA / PM and BM are to decide if a suitable single point of contact can be established to communicate and represent all RU and locations.
21. Where acceptance of works require an inspection, once agreed between the PMCA / PM and contractor, the PMCA / PM is to ensure applicable stakeholders, or their nominated representative, are invited for those inspections. Where applicable, stakeholders are to confirm (email or letter) that the delivered works meet the requirements associated with their organisation(s) requirements. i.e. Fuel Services Branch inspection / confirmation for Defence Fuel Installations.
22. The PMCA / PM can liaise with EMP and PAS PSS representatives to assist with identification of applicable stakeholders and obtaining their contact details.
Select HOTO Checklist and Project Lifecycle & HOTO Plan Criteria and Evidence
23. HOTO Checklist Signatures. This worksheet provides a summary of Project Lifecycle Criteria where the criteria status (Completed or Not Completed) is directly linked and automatically updated from the Project Lifecycle & HOTO Plan workbook. The HOTO Checklist Signatures page is used at the end of HOTO to signify that all project HOTO requirements have been met. The comment column on the signature page is a free text field that can be used by a stakeholder upon signing to alert the Zone Delegate of a potential risk or issue where verification has not yet occurred prior to their sign off and they are not the verifying authority. Any incomplete criteria is to be detailed in the HOTO caveat logs & DLP list and identify the required HOTO stakeholder signature/s. The PMCA / PM are to ensure accurate completion of the HOTO Checklist Signatures page and collect applicable stakeholder signatures before forwarding to the Zone EMP Representative for processing and sign off.
24. Project Lifecycle & HOTO Plan. This worksheet is a working document that records the agreed Project Lifecycle & HOTO criteria, evidence and status of completion. The document is to be managed, regularly reviewed and updated throughout the project lifecycle by the Contractor and validated by the PMCA / PM.
25. Data Provision Checklist (DPC). This worksheet is a working document that records the agreed project estate information and data requirements. i.e. Drawings, Operation & Maintenance Manuals (O&MMs), GEMS data, Master Site Plans etc. It aims to plan and set the estate information delivery requirements and validation points. It must be updated throughout the project lifecycle.
26. Selecting Criteria. At project commencement, the PMCA / PM, Zone EMP, PAS PSS and successful contractor must work through the proposed Project Lifecycle & HOTO Plan criteria and evidence, to select or adjust where necessary and agree the HOTO requirements. This is achieved by selecting in the Status Required column, "required" when the criteria is applicable and required for HOTO or selecting "N/A" when the criteria is not applicable to the project & HOTO. e.g. a Design Services Contract (DSC) Project Lifecycle & HOTO Plan will not require criteria relating to construction. When criteria are selected as "N/A", that criteria line will grey-out and de-activate auto functions in the form. Note: It's beneficial if the PMCA / PM and Zone EMP pre-populate the Project Lifecycle & HOTO Plan and evidence requirements in the pre-tender documents to minimise later adjustments. If further guidance is required about Project Lifecycle & HOTO Plan criteria and evidence requirements, the Project Lifecycle Criteria Instructions provide additional detail and links to relevant policy documents and manuals. For ease of reference, Project Lifecycle & HOTO Plan criteria have quick links to the corresponding section in the Project Lifecycle Criteria Instructions. This is achieved by ‘clicking’ on the criteria item number in the left-hand column. Similarly, criteria in the Data Provision Checklist should be reviewed and criteria applicable to the project determined. i.e. An estate works project may not have to create or update an O&MM or produce ASCONs due to the scope and nature of the works being delivered. Where DPC criteria / deliverables (rows) are not applicable or required for the project, "N/A" is to be selected in DPC column "D" - "Status Required". Refer to the DPC instructions Tab 7 for further information.
27. With agreement between the PMCA / PM, Zone EMP representative and contractor; HOTO criteria can be added and/or removed from the Project Lifecycle & HOTO Plan and Data Provision Checklist if deemed necessary as the project progresses. By including the HOTO activities as an agenda item in project progress meetings, changes to the Project Lifecycle & HOTO Plan can be discussed, agreed and documented in the minutes.
Acceptance of Works
28. The Project Lifecycle & HOTO Plan and Data Provision Checklist are to be continually reviewed at project meetings and progressively updated throughout the project lifecycle by the Contractor and validated by the PMCA / PM in consultation with the Zone EMP and PAS PSS. To record progress and complete the Project Lifecycle & HOTO Plan, the status column for required criteria should be assessed as ‘Completed’ or ‘Not Completed’. Where ‘Not Completed’ is recorded for HOTO, the comments field should briefly explain why e.g. caveats apply, requires defect rectification by a nominated date, seeking Defence dispensation etc., and/or make reference to location where more detailed explanation can be found, e.g. the issues register, Defects List etc.
29. When all criteria selected as "required" in a project phase are updated to "completed" in the "Status Completed" column, a summary status of "Completed" for that project phase appears in the title line and the HOTO Checklist Signatures page is automatically updated to complete in the status column for that phase. Where criteria are not completed at the end of each phase, an explanation is to be recorded and accepted in the comments field and details recorded in the HOTO Caveats Logs where applicable . The PMCA / PM is to ensure that all required criteria have been completed to the required standard before progressing to the next project phase. e.g. pre-mobilisation criteria that must be met prior to the commencement of construction or work on the Defence estate. At the end of the HOTO phase, a pdf copy of the completed checklist can be produced and sent to all specified stakeholders for review and acceptance via an electronic signature. Signed checklists are to be returned and saved on the project file.
30. The HOTO checklist can be signed by individual stakeholders even though there may be outstanding project deliverables not delivered, defects and/or conditions (which must be listed on the HOTO Caveat Logs). Consideration must be given as to the risk(s) the incomplete or defective item has to Defence including safety or the fit for purpose status of the delivered works. The defects, conditions or project deliverables not delivered should not be accepted when there has been ample notice and time during the delivery phase for the required deliverables to be achieved. It is highly desirable for the PMCA / PM to obtain all stakeholder signatures at the final HOTO meeting. However, if incomplete documentation does not allow this to occur, the contractor and PMCA / PM should first sign and then send a pdf copy of the signature page to all other stakeholders to simultaneously obtain signatures, before sending to the Zone EMP representative.
31. The Defence Representative or authorised delegate is responsible for accepting the delivered works from the CFI PD or PM into the Defence estate, for the purpose of TO and enabling its use by the resident unit (RU) for its intended purpose and initiating ongoing sustainment support e.g. Base Services Contract (BSC) services. For this to be achieved, the Zone EMP Representative is responsible to confirm that all HOTO Plan & Checklist criteria have been appropriately completed and if they have not, identify any risks associated with the outstanding items and that these items are recorded in the caveats log or defects list, confirm all required stakeholders have had sufficient opportunity to sign the checklist and prepare a recommendation and acceptance documents for the Defence Representative's action. The acceptance documentation is to include:
a. a copy of the HOTO Checklist Signatures and HOTO Caveat Logs; b. a copy of the contractor’s defect list and rectification plan; and c. any other documents that provide details and management of issues that may affect the safe operation and/or the fit for purpose state of the delivered works, these would generally be associated with any issues & caveats listed in the HOTO Caveats Log.
HOTO Approvals
32. The HOTO document provides for approvals (signatures) that must be obtained to achieve TO acceptance of the delivered works into Defence estate. The first signature is that of the Zone EMP Representative who is to provide a recommendation within the HOTO checklist for acceptance / rejection by the Defence Representative or authorised delegate. The signature provides assurance to Defence that the following has been achieved: a. stakeholder signatures have been obtained or an explanation provided as to why a particular stakeholder’s signature was not provided; b. works have been delivered and the applicable Certificate of Completion has been issued in accordance with the BWM, when applicable; c. stakeholders have been represented at the final inspection and any issues / concerns raised have been addressed and/or documented for resolution; d. there are no known non-conformances within the delivered works, or any non-conformances have been listed on the checklist as a caveat or condition to acceptance; and e. the project has provided all information necessary for Base Services Contractors to provide applicable maintenance and/or support services for safe occupation, use and ongoing sustainment.
33. The second signature is that of the Zone DSD (or delegate) who signs either: a. to “Approve’’ the TO acceptance of the delivered works into the Defence estate including the acceptance of any caveats and/or conditions listed; or b. as “Not Approved’’ noting the caveat(s) or condition(s) that must be rectified prior to TO acceptance by SDD.
HOTO Caveats Logs - Caveats or Conditions, Issues and Incomplete Project Deliverable
34. This section identifies project deliverables that have not been completed, are defective or are subject to a caveat or conditions. The Defence Representative may accept the defects or conditions to allow the estate to be used prior to delivery of all deliverables subject to the HOTO. There must be a rectification plan for any outstanding project defects or deliverables that include an agreed delivery date and the person responsible for ensuring delivery and fitness for purpose. The PMCA / PM must ensure accurate completion of the HOTO Caveat Logs and provision of an appropriate remediation plan before forwarding to the Zone EMP Representative with the completed HOTO Plan and Checklist.
35. Accepting a facility into service and use with outstanding defects or conditions will be decided on a risk basis. For example, outstanding or incomplete items of low risk to safety and operating or not compromising legislated compliance may be acceptable for conditional acceptance. Facilities not compliant with conditions specified in the BWM or un managed hazards will not be accepted for TO. The Defence Representative is the authority for these purposes.
Early Access or Use of Project Deliverables
36. There will be occasions in a project when a building and/or part of the project scope e.g. plant and equipment, needs to be accepted into operation and/or occupation prior to final project HOTO. Ideally these situations must be identified early as possible in the project lifecycle and separate HOTO Plan and Checklists be assigned, i.e. project planning / design phases or early in the construction phase. These situations may occur due to: a. operational imperatives; b. requirement to decant occupants from a building that must demolished and/or refurbished by the project; or c. energise an electrical sub-station that powers new and existing facilities etc.
37. Where occasions as described above occur later in the project construction phase and a separate HOTO Plan & Checklist was not arranged or exceptional circumstances make it impractical to arrange, conditional TO acceptance for operation and/or early occupation can occur before the final project HOTO. To administer a conditional acceptance, the HOTO Plan and Checklist must be completed as much as reasonably practical and all outstanding requirements and deliverables required to complete the HOTO are documented in the HOTO Caveat Logs, accompanied with a delivery plan. The Defence Representative or authorised delegate are the approval authority for a conditional TO acceptance. Therefore they must be satisfied that the HOTO Plan and Checklist is sufficiently complete, all outstanding HOTO items & requirements are documented (as listed on the HOTO caveat logs), the residual level of risk is manageable and required sustainment service can be provided by applicable BSCs. The Defence Representative or authorised delegate must consider the following conditions to assist in making this determination:
a. The contractor demonstrates that buildings and/or equipment are fit for purpose, safe to occupy and operate via the provision of a certificate of completion and other applicable legislative / policy required licences and/or conformance certificates, etc. b. PMCA / PM confirmation that all deliverables associated with the building and/or equipment have been completed, and where this is not achieved, a list of outstanding items and delivery plan is provided. c. Provision of a defects list and acceptable rectification plan. d. Provision of a building and/or equipment support and maintenance plan that covers the period up to HOTO finalisation. e. Receipt of PAS notification that they and applicable BSC contractors are prepared, sufficiently trained and capable of providing the required sustainment support for the building and/or equipment. This includes establishing interim measures to deliver services where CCPs are not yet approved e.g., via a survey and quote. f. The Zone EMP confirms that the conditions above have been met and provides a recommendation that supports conditional TO acceptance.
End of Defects Liability Period
38. During DLP the contractor, PMCA / PM, PAS PSS and Zone EMP representative must work collaboratively towards clearing all actions recorded on the HOTO Caveat Logs and contractor’s defect list and rectification plan. At the end of DLP, the PMCA / PM is to ensure that all DLP checklist criteria have been satisfied by the specified responsible person/s, suitable evidence of completion is provided and acceptance of DLP stakeholders is completed before forwarding to the Zone EMP representative for final approval.

## 0. Project Details
Project Details | Details (insert below) | Guide | Status | Required | N/A | Approved
Project Number: |  | This is the project number given to the project by the PMCA / PM (e.g. NAT-02-0529) |  | Completed | N/A | Not Approved
Project Name: |  | This is the project name given to the project by the PMCA / PM (e.g. HMAS STIRLING Defence Fuel Installation (DFI) Remediation) |  | Not Completed |  |  |  | "Select from Drop down menu"
Project Source | "Select from Drop down menu" | This is the project source (e.g. CFI, Estate Works Program, property acquisitions and disposals and PMB leased projects) | [5 empty] | CFI
Project Location: |  | State and Establishment Number (e.g. WA, 0089 HMAS STIRLING) | [5 empty] | EWP
Building/Assets Description & HOTO Descriptor: |  | Building description (e.g. DFI-M, DFI-M Wharf Area, Small Boats ect & HOTO Descriptor where applicable (e.g. To differentiate between multiple HOTOs use on one project. HOTO 1 of 5 - Stage 5 - New Aviation Fuel Farm) | [5 empty] | Property Acquisition or Disposal
Building/Assets Number(s): |  | e.g. A0061, A0068 | [5 empty] | PMB Leased Project
Project Start Date: |  | The actual project start date or the Estate Works Program year (e.g. the Financial Year). | [5 empty] | Other
Handover/Takeover Inspection: |  | The date the HOTO inspection took place. |  |  |  | N/A | Completed
Project Completion Date: |  | The actual project completion date.
DLP Maintenance Agent: |  | Detail what entity will provide maintenance during DLP. e.g. Contractor's agent or PAS.
WOL Maintenance Agent: |  | Detail what entity will provide maintenance Post DLP. e.g. PAS, Defence Fuel Network Managing Contractor, etc.
Project Document Location: |  | Objective location for the project file with all HOTO documents and evidence etc.
Project Stakeholders | Stakeholder Name, Title, Organisation (insert below) | Guide
CFI Project Director / PDS Project Manager or any Defence entity project manager |  | The approved Defence or contracted project manager representative.
Project Manager Contract Administrator (PMCA) |  | This is the Consultant on-site representing the PD.
Zone Estate Management & Planning (EMP) Representative |  | This is the Zone specific representative on behalf of Defence.
Zone Environment & Sustainability (ES) Representative |  | This is the Zone specific representative for environment matters on behalf of Defence.
Base Manager |  | The BM applicable to the project Base Support Area.
Sponsor or User Group Representative |  | This is the Capability Manager and/or project sponsor; or their appointed representative. Consider if a suitable single POC can be established to communicate and represent all RU and locations.
PAS Project Support Service (PSS) Representative |  | This is the PAS PSS representative.
Contractor |  | This is the delivery Contractor.
Subject Matter Experts (SME) (as applicable) |  | i.e. DELM, DEWPO, Environment & Engineering Branch, Property Management Branch, Fuel Services Branch (FSB), JLOG, Explosive Ordnance Branch, Security, JCG, DS&VS, ESA (ADF Security), EGIS Policy owners, PAS SME etc.
[Insert Others]
[Insert Others]
[Insert Others]
[Insert Others]
[Insert Others]
[Insert Others]
[Insert Others]
[Insert Others]
Verifying Persons
CFI Project Director / PDS Project Manager or any Defence entity project manager
PDS or PMCA
Zone EMP Representative
PAS PSS Representative
Responsible Persons
PDS or PMCA
Zone EMP Representative
Zone ES Representative
Sponsor or User Group Representative
PAS PSS Representative
Contractor (Designer)
Contractor (MC / HC)
SME - Specify

## 1. HOTO Checklist Signatures
HOTO Checklist Signatures
Please enter project details into '0. Project Details' tab
Project Location:
Building/Assets Description & HOTO Descriptor:
Building/Assets Number(s):
Project Document Location:
| Phase | Status | Person Verifying Completion |  | Comments
1 | Project Planning & Development Phase | Not Completed | Zone EMP Representative
2 | Design | Not Completed | PMCA/PM
3 | Pre-Mobilisation | Not Completed | PMCA/PM
4 | Construction and Commissioning | Not Completed | PMCA/PM
5 | Handover Takeover (HOTO) | Not Completed | PMCA/PM
Stakeholder Signatures
HOTO Key Stakeholder |  | Name |  | Signature |  | Date Signed | Comments
CFI Project Director / PDS Project Manager or any Defence entity project manager |  | 0
Project Manager Contract Administrator (PMCA)
Contractor
Base Manager
Sponsor or User Group Representative
PAS Project Support Service (PSS) Representative
Subject Matter Experts (SME) (as applicable)
Note: The above signatures confirm stakeholder engagement, acknowledging that the project meets the requirements of the HOTO Plan & Checklist in accordance with Defence requirements. The buildings and assets presented for HOTO are without any outstanding issues that preclude safe occupancy or fit for purpose use and all issues are captured correctly in the applicable log for action and resolution by the project team. If the signatory is aware of any risks or issues that may impact safe occupancy or fit for purpose use to which they are not the verifying authority, please detail in the comment column for consideration by the defence delegate.
ACCEPTANCE DETAILS
Zone Representative |  | (Zone Estate Management & Planning member)
Recommendedation: |  | Recommended / Recommended with Caveats / Not Recommended
Name:
Signature:
Date:
Defence Representative |  | (Zone Director Service Delivery (DSD) or authorised delegate - e.g., AD EMP)
Recommendedation: |  | Recommended / Recommended with Caveats / Not Recommended
Name:
Signature:
Date:
Secondary Defence Representative if required. (i.e. FSB) |  | Status: | N/A
Recommendedation: |  | Recommended / Recommended with Caveats / Not Recommended | [5 empty] | Required
Name: | [7 empty] | N/A
Signature:
Date:
This section auto populates from: 2. Proj Lifecycle & HOTO Plan.

## 2. Proj Lifecycle & HOTO Plan
Project Lifecycle & HOTO Plan
Project Name: | 0 | Project Location (State): |  | 0 | Building/Assets Description & HOTO Descriptor:
Project Number: | 0 | Building/Assets Number(s): |  | 0
Item number is hyperlinked to Proj Lifecycle Criteria Instructions
Item | Criteria | Status Required | Responsible Person | Evidence Type | Status Completed | Verifying Person | Comments | Project Lifecycle Phase
| Project Planning & Development Phase |  |  |  | Not Completed
1 | Project start meeting held where key Stakeholders are identified and Project HOTO requirements are discussed and confirmed including:- - Clarification of Project Scope - Provision of Baseline Project Schedule - Access provided to project web based document management systems | Required | PMCA/PM | A copy of the project start meeting minutes. If not addressed in the minutes, also provide a copy of: * List of key project stakeholders and their ongoing role / required meeting requirements. *Acknowledgement that key stakeholders received & agree (where applicable) the project scope of works. *Copy of IBC or DBC authorities page. *Baseline Project Schedule * An email from the PMCA / PM advising data system access arrangements and list of stakeholders provided access . | Not Completed | Zone EMP Representative |  | Planning & Development
1.1 | Project HOTO Plan and Checklist | Required | PMCA/PM | Provision of an agreed HOTO plan & checklist. | Not Completed | Zone EMP Representative |  | Planning & Development
| Design Phase |  |  |  | Not Completed
2 | Design initiation start meeting to confirm stakeholders, scope and design requirements. | Required | Contractor (Designer) | * Email from PMCA / PM advising that criteria is met and a copy of the minutes are saved in Objective or for CFI, the mandated project information management system. * Copies of design review meeting minutes and/or correspondence from key stakeholders and SMEs acknowledging design input and/or acceptance. | Not Completed | PMCA/PM |  | Design
2.1 | Estate Information Provision Plan (EIPP) and Data Provision Checklist created and agreed. (Refer Tab 3 DPC & Tab 8 EIPP Template) | Required | Contractor (Designer) | Provide copy of agreed EIPP and DPC. | Not Completed | PMCA/PM |  | Design
2.2 | Compliant Design Where required:- * approved performance solutions IAW Building Works Manual (BWM) * approved Dispensation IAW the Building Works Manual (BWM). | Required | Contractor (Designer) | Where applicable and in accordance with Estate Engineering Policy Provide: *Copies of designer certifications for all applicable aspects. *Where designs require other SME endorsement like FSB, EO and JCG; provide a copy of SME certification notice. *Copy of the approved performance solution prior to the issue of a building approval. The "Request for Performance Solution Template" can be found under the templates link on the Engineering Policy - Building Works page. *Copy of the approved dispensation request prior to issue of a building approval. The "Request for Dispensation Template" via the Estate Engineering Policy page. *Copy of Electrical Development Plan where Electrical Network or Base Supply works have been undertaken. | Not Completed | PMCA/PM |  | Design
2.3 | Design considerations:- * Safety in design conducted and findings accepted * MFPE Design requirements for Bushfire Prone Areas. *Smart Infrastructure in Design * Security in Design | Required | Contractor (Designer) | Where applicable and in accordance with EGIS, BWM & MFPE provide: *Design review documentation identifying any hazards requiring treatment, i.e. a register and associated risk management measures. *Email demonstrating DS&VS engagement and where applicable, details of SCEC engaged consultant. *Email demonstrating Base Manager and Zone ESO engagement for risk assessment and treatment designs (for example through APZs). *Copy of completed Smart Infrastructure Checklist provided in Smarti Manual. | Not Completed | PMCA/PM |  | Design
2.4 | PAS input to design, whole-of-life and DLP maintenance requirements. | Required | PAS PSS | A copy of invitation correspondence (email or other) issued to PAS and PAS confirmation of attendance and/or provision of feedback. | Not Completed | PMCA/PM |  | Design
2.5 | Building Contribution Factor for new built facilities, new leases or where the building work changes the CF of an existing building. | Required | Sponsor or User Group Representative | Email from Capability Manager (ASEP or delegate) where applicable to indicate that the Building Contribution Factor Form is provided for file and the form has been submitted. Email from Capability Manager (ASEP or delegate) to indicate that no change is required (for existing facility). If a change is required, a copy of the Building Contribution Factor Form is provided for file and BM / Capability Manager (or delegate) advise the form has been submitted or copy of DBC approval page. | Not Completed | PMCA/PM |  | Design
2.6 | Site Selection Board Completed and Approved | Required | PMCA/PM | A copy of the site selection recommendation(s) approved by the Delegate. For CFI project - a copy of the IBC or DBC approvals page. | Not Completed | Zone EMP Representative |  | Design
2.7 | PAS Information Pack | Required | PAS PSS | An email from the PDS or PMCA to confirm receipt of PAS Information pack for inclusion into HC / MEWC tenders or copy of minutes where receipt has been noted. | Not Completed | PMCA/PM |  | Design
2.8 | Data Provision Checklist Actions & Deliverables have been completed and verified for Design Phase | Required | Contractor (Designer) | Design Phase of the Data Provision Checklist Completed | Not Completed | PMCA/PM |  | Design
| Pre-mobilisation Phase |  |  |  | Not Completed
3 | Pre-mobilisation start meeting held with stakeholders, scope of works and design confirmed and Project commissioning & HOTO Plan & Checklist, DLP outline maintenance plan, training requirements identified and delivery plan all agreed by HOTO key stakeholders | Required | Contractor (MC / HC) | Copy of meeting minutes. Copy of agreed HOTO Plan & Checklist. If not recorded in the meeting minutes, a copy of the agreed (with PAS) DLP outline maintenance plan, where applicable. | Not Completed | PMCA/PM |  | Pre-mobilisation
3.1 | Estate Information Provision Plan (EIPP) and Data Provision Checklist created and agreed. (Refer Tab 3 DPC & Tab 8 EIPP Template) | Required | Contractor (Designer) | Copy of agreed Estate Information Provision Plan (EIPP) and Data Provision Checklist (DPC). | Not Completed | PMCA/PM |  | Pre-mobilisation
3.2 | Site Management Plan/s. | Required | Contractor (MC / HC) | Evidence to include copy of correspondence to Base & PAS of agreed Site Management Plan/s. | Not Completed | PMCA/PM |  | Pre-mobilisation
3.3 | Dilapidation Surveys | Required | Contractor (MC / HC) | PMCA / PM email notification of receipt of dilapidation survey. | Not Completed | PMCA/PM |  | Pre-mobilisation
3.4 | Notification of Demolition | Required | Contractor (MC / HC) | A copy of the email submission of Notification of Demolition form and provision to PAS PSS. | Not Completed | PMCA/PM |  | Pre-mobilisation
3.5 | Asset Rollout Notification form Prepared & Submitted (Asset Valuation) for all new or refurbished facilities. | Required | PMCA/PM | A copy of the Asset Rollout Notification email submission. | Not Completed | Zone EMP Representative |  | Pre-mobilisation
3.6 | Environmental Clearance Certificate (ECC - form AB081) submitted and approved by Zone ESO, including an Environmental Management Plan (EMP) where relevant. | Required | Contractor (MC / HC) | A copy of the approved ECC by the Zone ESO. | Not Completed | PMCA/PM |  | Pre-mobilisation
| Construction Phase |  |  |  | Not Completed
4 | PAS has established maintenance and support (including relevant MSP's or Other Maintenance Agent) by: CFI Projects - 28 day notice of completion, All other projects by 90% construction. | Required | PAS PSS | PAS email correspondence confirming that the required PAS and MSP operational and maintenance support is ready to proceed at facility handover and occupation / use. | Not Completed | PMCA/PM |  | Construction
4.1 | Contractor to provide a Commissioning and Training Plan | Required | Contractor (MC / HC) | PAS email correspondence confirming that they have reviewed and support applicable Commissioning, ITP and training plans. | Not Completed | Zone EMP Representative |  | Construction
4.2 | Data Provision Checklist Actions & Deliverables have been completed and verified for the Construction Phase. | Required | Contractor (Designer) | Construction Phase of the Data Provision Checklist Completed | Not Completed | PMCA/PM |  | Construction
| Commissioning |  |  |  | Not Completed
4.3 | Approval from the Defence Electrical Operating Authority (Network Controller) prior to de-energising or energising the electrical infrastructure network | Required | Contractor (MC / HC) | Authority to connect or disconnect to or from the electrical distribution system approved by the Network Controller. | Not Completed | Zone EMP Representative |  | Commissioning
4.4 | Pre-commissioning approvals and notifications completed IAW agreed contractor’s commissioning and HOTO Plan & Checklist | Required | Contractor (MC / HC) | Copy of Email notification from applicable Technical authority advising approval to proceed with commissioning. | Not Completed | PMCA/PM |  | Commissioning
4.5 | Training and / or “train-the-trainer” training provided by the contractor on all facility systems for the operators and maintainers | Required | Contractor (MC / HC) | Training provided for the operator and maintainer and/or train-the-trainer a. a copy of the training syllabus; b. a list of attendees and the competency levels achieved; and c. PAS email confirmation is provided stating the training is completed in accordance with the requirements agreed to satisfy HOTO criteria 3.0 | Not Completed | PMCA/PM |  | Commissioning
| HOTO Phase |  |  |  | Not Completed
5 | Design & Build Compliance Construction completed to approved design and all variations to original design IAW the BWM requirements. | Required | Contractor (MC / HC) | Certificate of Completion for each building and a copy of the staged occupancy plan. Copy of approved dispensation submission / form. If applicable. Copy of approved performance solution submission / form. If applicable. | Not Completed | PMCA/PM |  | HOTO
5.1 | Defect Liability Period (DLP). DLP management procedure provided, defects list & rectification schedule provided by the contractor representative including any register of outstanding defects, non-delivered project outcomes and rectification plan. | Required | Contractor (MC / HC) | DLP management procedure. This may be in a flow chart. Email from PAS acknowledging acceptance of procedure. Copy of Defects list and rectification schedule. Provision of agreed HOTO Caveat Log. (Refer to Tab 5) | Not Completed | PAS PSS |  | HOTO
5.2 | Unexploded Ordnance (UXO) certifications with maps and GPS points of boundaries clearance (plus to the required depth) | Required | Contractor (MC / HC) | Where applicable, an email confirming that all UXO certificates and data have been submitted to nuxo.program@defence.gov.au and uxo@defence.gov.au | Not Completed | PMCA/PM |  | HOTO
5.3 | Services Surveys and Testing Reports | Required | Contractor (MC / HC) | A list of all services surveys and testing reports provided, where applicable. Email notification from PMCA / PM, PAS PSS and/or EMP (where applicable) that listed reports where received for saving on Objective. | Not Completed | PMCA/PM |  | HOTO
5.4 | Handover key schedule completed and attached with full set of tagged keys provided | Required | Contractor (MC / HC) | At HOTO consolidated list of keys and a signed transfer sheet; and where SCEC hardware is applicable, written notification from the specified applicable Security Officer that keys and key / hardware list have been received. | Not Completed | Zone EMP Representative |  | HOTO
5.5 | High Risk Plant or Equipment essential operating instructions and/or diagrams and relevant logbooks are in place and certification certificates provided | Required | Contractor (MC / HC) | Email from PMCA / PM that Defence requirements for essential operating instructions and/or diagrams have been met. A list of logbooks and wiring diagrams and email from PAS stating satisfaction with their provision / placement. | Not Completed | Zone EMP Representative |  | HOTO
5.6 | Registerable Plant essential operating instructions and/or diagrams, logbooks, test certificates are in place including design registration. | Required | Contractor (MC / HC) | A list of: Registerable Plant operating instructions, diagrams and / or logbooks, test certificates displayed at equipment and the location for each item listed. Copy of Design Registration Certificates. Email from PAS PSS stating satisfaction with their provision / placement | Not Completed | Zone EMP Representative |  | HOTO
5.7 | Radiation safety considerations i.e. Radiation Apparatuses (removal or addition) | Required | Contractor (MC / HC) | Where applicable provide: A copy of any DRSA notification. Completed AE168, Completed AD824, | Not Completed | PMCA/PM |  | HOTO
5.8 | Emergency Evacuation Plans provided electronically and physically attached to the facilities. | Required | Contractor (Designer) | Certificate of Completion. Provide a list of where Emergency Evacuation Plans have been updates and/or supplied new – where applicable. Provide an electronic copy of plans. | Not Completed | PMCA/PM |  | HOTO
5.9 | Notifying critical equipment and / or critical spares | Required | Contractor (MC / HC) | PAS PSS to provide an email acknowledging receipt of an applicable critical asset & spares list. | Not Completed | PAS PSS |  | HOTO
5.1 | All Fire Safety Systems, Equipment, Monitoring, Alarm and Suppression System Installations meet applicable AS, MFPE and NCC requirements. | Required | Contractor (MC / HC) | Applicable ITPs and ITRs. Installation Certificates. Email from PAS PSS confirm successful operation when integrating into existing systems. | Not Completed | PMCA/PM |  | HOTO
5.11 | Electrical Test Certificates | Required | Contractor (MC / HC) | Certification / statement of compliance: a. Installation certificate; b. Evidence of electrical load balancing over all 3 phases; c. ITPs & ITRs and electrical safety certificates, d. Switching authority certification with Hazardous areas (when applicable) | Not Completed | PAS PSS |  | HOTO
5.12 | Hazardous Area and Explosives Area Verification Dossier | Required | Contractor (MC / HC) | An compliant Hazardous Area and Explosives Area Verification Dossier | Not Completed | PAS PSS |  | HOTO
5.13 | Mechanical test & commissioning results | Required | Contractor (MC / HC) | ITPs and ITRs. Installation Certificates. | Not Completed | PMCA/PM |  | HOTO
5.14 | Hydraulic test & commissioning results | Required | Contractor (MC / HC) | ITPs and ITRs. Installation Certificates. | Not Completed | PMCA/PM |  | HOTO
5.15 | Security inspections have been completed and passed | Required | Contractor (MC / HC) | Certificate of compliance with the appropriate security requirements, and inspection report from Defence Security Unit (where applicable). | Not Completed | PMCA/PM |  | HOTO
5.16 | Physical Security Certification | Required | Contractor (MC / HC) | Final inspection report from the certified security agency or an email advising a final inspection is not required. A report must include photographic evidence and close up inspections where required e.g. ceiling spaces and voids, approved variations are documented and SCEC consultant sign off that the construction meets the security design. | Not Completed | PMCA/PM |  | HOTO
5.17 | Commissioning for security systems, alarms, and access control systems including training | Required | Contractor (MC / HC) | Facility Certification from DS&VS, ADF ESA or ASIO-T4 (for Security Zone 5). Installer commissioning documentation and SCEC consultant sign off for Type1A alarm systems. Email from PAS PSS to confirm successful operation when integrating into existing systems. | Not Completed | PMCA/PM |  | HOTO
5.18 | O&MM for security systems, alarms and access control systems provided to Unit Security Officer | Required | Contractor (MC / HC) | Email from Facility Security Officer acknowledging and accepting receipt of applicable items. i.e. O&MM, keys and access codes and/or combinations. | Not Completed | Zone EMP Representative |  | HOTO
5.19 | Certification / Accreditation for Sensitive Compartmented Information Facilities (SCIF), Magazines and Armouries and Zones 2 to 5. | Required | Contractor (MC / HC) | Certification / statement of compliance from the installation contractor stating what the installation complies with SCIF construction plan and armoury construction guidelines. Copy of the assessment certificate / notice from the inspection & accreditation agency advising the facilities comply with Defence required policy and standards. . | Not Completed | Zone EMP Representative |  | HOTO
5.2 | Updated Defence Engineering Service Network (DESN) configuration and management documentation impacted by project works | Required | Contractor (MC / HC) | ITR for commissioning. Email from PAS PSS verifying successful operation when integrating into existing systems. | Not Completed | PMCA/PM |  | HOTO
5.21 | Voice and Video Phones system commissioned and connected to existing base infrastructure | Required | Contractor (MC / HC) | Commissioning ITPs and ITRs, Email from JCG or Telstra verifying successful operation and/or integrating into existing systems (where applicable). | Not Completed | PMCA/PM |  | HOTO
5.22 | Defence Data Networks (Passive infrastructure works) are commissioned and connected to existing base infrastructure. | Required | Contractor (MC / HC) | A list of all security items and/or network drawings handed to ICT which has been signed as correct by JCG and/or Telstra where applicable. | Not Completed | PMCA/PM |  | HOTO
5.23 | Keys for communications rooms, cabinets and infrastructure pits have been installed to Defence Security Principles Framework (DSPF) and Information Security Manual (ISM) standards and handed over to Regional ICT | Required | Contractor (MC / HC) | A list of all security items handed to ICT which has been signed as correct by JCG and/or Telstra where applicable. Copy of signed receipt from JCG / Telstra | Not Completed | PMCA/PM |  | HOTO | PDS or PMCA
5.24 | ICT systems commissioned and accepted by JCG | Required | Contractor (MC / HC) | Commissioning ITPs and ITRs, JCGG Corp System. Email from JCG or Telstra verifying successful operation and/or integration into existing systems (where applicable). BMS. Email from PAS verifying successful operation and/or integration into existing systems Capability Systems. Email for Capability Manager verifying successful operation and/or integration into existing systems. | Not Completed | PMCA/PM |  | HOTO | Zone EMP Rep
5.25 | List of all hazardous chemicals - quantity / type and storage system of fuels, chemicals or lubricants for uploading into ChemAlert. | Required | Contractor (MC / HC) | A complete list of hazardous materials to Base management team, resident unit and/or PAS where applicable. Email copy of receipt from Base RU and / or PAS. | Not Completed | PMCA/PM |  | HOTO | (Designer) Contractor Rep
5.26 | ECC Post Activity Report (PAR) Signed. | Required | Contractor (MC / HC) | A copy of signed PAR. | Not Completed | PMCA/PM |  | HOTO
5.27 | Reporting Environmental Incidents | Required | Contractor (MC / HC) | Copy of GEMS incident Report Form - or GEMS ref # | Not Completed | PMCA/PM |  | HOTO
5.28 | Provision of Contaminated Sites Management Plan. | Required | Contractor (MC / HC) | Evidence to include copy of correspondence to Base & PAS of agreed Contaminated Sites Management Plan and update of contamination site register. | Not Completed | PAS PSS |  | HOTO
5.29 | Provision of Environment Protection and Sustainability Management Plan. | Required | Contractor (MC / HC) | Evidence to include copy of correspondence to Base & PAS of agreed Environment Protection and Sustainability management plan. | Not Completed | PAS PSS |  | HOTO
5.3 | Heritage management information provided for Heritage Management Plan | Required | Contractor (MC / HC) | Copy of Heritage Management report provided to the Zone ESO. | Not Completed | PMCA/PM |  | HOTO
5.31 | Smart Infrastructure requirements complete | Required | Contractor (MC / HC) | Provision of completed Smart Infrastructure Checklist (Smarti) | Not Completed | PMCA/PM |  | HOTO
5.32 | Billing connection & dis-connection of energy; including solar, gas and water services. | Required | Contractor (MC / HC) | Copy of submitted AE879. | Not Completed | PMCA/PM |  | HOTO
5.33 | Software Provision of system software, software licences and all configuration files | Required | Contractor (MC / HC) | Software licence certificates, and email notice of receipt (EMP and/or PAS) for backed up copy of software and/or configuration files. | Not Completed | PMCA/PM |  | HOTO
5.34 | Data Provision Checklist Actions & Deliverables have been completed and verified for HOTO Phase. | Required | Contractor (Designer) | HOTO Phase of the Data Provision Checklist completed. | Not Completed | PMCA/PM |  | HOTO
5.35 | Asset Rollout pack Completed & Submitted for all new or refurbished facilities. | Required | PMCA/PM | A copy of the complete Asset Rollout email submission. | Not Completed | Zone EMP Representative
| Transition |  |  |  | Not Completed
5.36 | PAS PSS has attended site to confirm services for support in preparation for maintenance on Takeover | Required | PMCA/PM | Minutes / Report for the final walk around activities that clearly document attendees and acceptance of outcomes / actions. | Not Completed | Zone EMP Representative |  | Transition
5.37 | Relevant support, services and maintenance for Base Services Contracts have been actioned and accepted by relevant service provider/s in preparation for DLP commencement. | Required | PAS PSS | Email from PAS PSS confirming Service Provider/s acceptance of support, services and maintenance. | Not Completed | Zone EMP Representative |  | Transition
| DLP Phase |  |  |  | Not Completed
6 | All Defence approved HOTO caveats and issues cleared | Required | PMCA/PM | PMCA / PM email confirming that all approved HOTO caveats and issues have been cleared, and required evidence is stored on the DEIS. | Not Completed | Zone EMP Representative |  | DLP
6.1 | NLT 28 days prior to DLP end date, all defects repaired and related estate data has been updated | Required | Contractor (MC / HC) | End DLP checklist and Defects log completed, suitable evidence (as detail in the agreed defect rectification plan) is provided. | Not Completed | PMCA/PM |  | DLP
6.2 | 28 days prior to DLP end date, PAS advised and confirmed their readiness to commence agreed maintenance at the end of DLP (for CFI & by exception for EWP). | Required | PAS PSS | A confirmation letter or email from PAS PSS. | Not Completed | PMCA/PM |  | DLP
6.3 | Data Provision Checklist Actions & Deliverables have been completed and verified for DLP. | Required | Contractor (Designer) | Completed copy of Data Provision Checklist for DLP Phase. | Not Completed | PMCA/PM |  | DLP
6.4 | Final Asset Rollout submission, including Works undertaken during DLP that add value to the asset/s. | Required | Contractor (MC / HC) | A copy of the Final Asset Rollout email submission. | Not Completed | Zone EMP Representative |  | DLP

## 3. Data Provision Checklist
Project Details |  | Data Provision Checklist
Project Number: |  | 0
Project Name: |  | 0
Building/Assets Number(s): |  | 0
Project Location (State): |  | 0
Building/Assets Description & HOTO Descriptor:
EIPP Endorsed by PMCA / PM
Project Phase |  | Data Provision Actions and Deliverables (DPC Criteria) | Status Required | Responsible Person | Planned Completion Date | Completion Date | Comments
Design
1 | Design | Data Extracts from GEMS provided to Designer (required for existing facilities, extending current infrastructure and/or upgrading existing assets) | Required | (request) PMCA / PM (supply) PAS - Data extracts (supply) PAS - Spaces Plan
2 | Design | The Project submits a GDL to PAS PSS requesting to create asset shell records for Buildings, Levels, Spaces, Infrastructure, Equipment Systems & Equipment (where known) etc. and provides a new or updated spaces plan. GDL and Spatial Data submissions are accompanied by relevant Assurance & Validation Checklists | Required | Designer
3 | Design | PAS review GDLs and process in EDGA. Incorrect submissions are quickly referred back to supplier with detail about issues. | Required | PAS PSS
4 | Design | All required GDLs to create shell records have been submitted to PAS PSS by the 90% design - Building, Level, Space, Infrastructure, Equipment Systems & Equipment (where known) etc. | Required | Designer
5 | Design | A list of compliant design drawings, minutes of design meetings and/or correspondence from stakeholders and SMEs identified in the agreed EIPP accepting designs. Design Drawings Completed - End of design phase. | Required | Designer
6 | Design | Spaces Plan prepared IAW SDMP and submitted with completed SDMP Assurance & Validation Checklist. | Required | Designer
Construction
7 | Pre-mobilisation | Data Extracts from GEMS provided to Contractor Representative (required for existing facilities, extending current infrastructure and/or upgrading existing) | Required | (request) Contractor (supply) PAS
8 | Construction | The Project submits GDLs with completedAssurance & Validation Checklist to PAS PSS requesting to Create asset shell records and / or Update asset records. Incorrect submissions are quickly referred back to supplier with detail about issue areas. | Required | Contractor
9 | Construction | Additional GDL submissions, as required & determined by project. (all data for new or updated items is to be supplied via GDL by 90% construction). | Required | Contractor
10 | Construction | PAS review GDLs and process in EDGA. Incorrect submissions are quickly referred back to supplier with detail about issues | Required | PAS PSS
11 | Construction | RFI Notice to request Master Site Plan (MSP) for Update purposes issued to PAS PSS. | Required | PMCA/PM
| 28 Day notice of Completion (CFI project) or 90% construction for all other projects. |  | Required
12 | Construction | Submission of all GDLs with accompanying GDL Assurance & Validation Checklist to PAS PSS - all data fields completed. | Required | Contractor
13 | Construction | Submission of draft O&MM with accompanying O&MM Assurance & Validation Checklist for validation. | Required | Contractor
14 | Construction | Submission of draft As Constructed drawings to PAS PSS with accompanying Assurance & Validation Checklist for validation. | Required | Contractor
15 | Construction | Submission of draft updated and/or new MSP and Spaces Plan to PAS PSS with accompanying Assurance & Validation Checklist for validation. | Required | PMCA/PM
16 | Construction | PAS review GDLs and process in EDGA. Incorrect submissions are quickly referred back to supplier with detail about issues. | Required | PAS PSS
17 | Construction | PAS PSS feedback on draft O&MMs | Required | PAS PSS
18 | Construction | PAS PSS feedback on draft ASCON drawings | Required | PAS PSS
19 | Construction | PAS PSS feedback on draft MSP and Spaces Plan | Required | PAS PSS
Hand Over Take Over (HOTO)
20 | HOTO | Submission of all GDLs are delivered in accordance with the contract requirements and agreed changes implemented. | Required | Contractor
21 | HOTO | All final ASCON drawings and single line diagrams are delivered with agreed changes implemented. | Required | Contractor
22 | HOTO | All final O&MMs are delivered with agreed changes implemented. | Required | Contractor
23 | HOTO | Final updated and/or new MSP and Spaces Plan delivered with agreed changes implemented. | Required | Contractor
24 | HOTO | PAS PSS confirm all GDLs have been received, accepted and provided to the GEMS MDT for upload. | Required | PAS PSS
25 | HOTO | PAS PSS confirm all ASCON drawings received and agreed changes are complete. | Required | PAS PSS
26 | HOTO | PAS PSS confirm all O&MM received and agreed changes are complete. | Required | PAS PSS
27 | HOTO | PAS PSS have reviewed and accepted Key Datasets (Mater Site Plan (MSP) and Spaces Plan) | Required | PAS PSS
Defect Liability Period (DLP)
28 | DLP | GDLs submitted as a result of defect rectifications | Required | Contractor
29 | DLP | O&MM, ASCONs and/or MSP updated as a result of defect rectifications | Required | Contractor
30 | DLP | PAS PSS confirm that all information submissions received for criteria 28 & 29 are compliant and suitable for uploading to the applicable Defence system. | Required | PAS PSS
Note on D9: Nicholls, Gavin MR: Select N/A where DPC criteria are not applicable or required by the project.
Note on E9: Nicholls, Gavin MR: Entity responsible to fulfil the action
Note on F9: Nicholls, Gavin MR: To be completed by the Contractor in consultation & agreement with PMCA / PM, PSS & EM&P Rep
Note on G9: Nicholls, Gavin MR: To be completed by the PMCA / PM
Note on A11: Gavin: Click on number to link to corresponding instructions
Note on C19: (insert additional rows below if multiple batches of GDLs requesting to Create or Update records, as scheduled on different dates throughout the construction period)
Note on C20: Gavin: Submission of GDLs throughout construction phase (GDL submissions can be grouped to logical work elements depending on nature of project. Add lines below to indicate schedule for additional GDL delivery times)
Note on C21: Gavin: Add lines below to align with contractors schedule for multiple GDL delivery times.
Note on C28: Gavin: Add lines below to align with contractors schedule for multiple GDL delivery times.

## 4. DLP Checklist
DLP Checklist
Please enter project details into 0. Project Details Tab
Project Location: | 0
Building/Assets Description & HOTO Descriptor: | 0
Building/Assets Number(s): | 0
Project Start Date: 00-Jan-1900 ¦ HOTO Inspection: 00-Jan-1900 ¦ Project Completion Date: 00-Jan-1900
DLP Start and Finish Dates
DLP Maintenance Agent:
END OF DEFECT LIABILITY PERIOD
Item | Defects Liability Period (DLP) & Project End | Status |  | Person Verifying Completion | Comments
|  | Required | Completed
6 | All Defence approved HOTO caveats and issues cleared | Required | Not Completed | Zone EMP Representative
6.1 | NLT 28 days prior to DLP end date, all defects repaired and related estate data has been updated | Required | Not Completed | PMCA/PM
6.2 | 28 days prior to DLP end date, PAS advised and confirmed their readiness to commence agreed maintenance at the end of DLP (for CFI & by exception for EWP). | Required | Not Completed | PMCA/PM
6.3 | Data Provision Checklist Actions & Deliverables have been completed and verified for DLP. | Required | Not Completed | PMCA/PM
6.4 | Final Asset Rollout submission, including Works undertaken during DLP that add value to the asset/s. | Required | Not Completed | Zone EMP Representative
Stakeholder Signatures
HOTO Key Stakeholder |  | Name |  | Signature | Date Signed
CFI Project Director / PDS Project Manager or any Defence entity project manager |  | 0
Project Manager Contract Administrator (PMCA)
PAS Project Support Service (PSS) Representative
ACCEPTANCE - END OF DEFECT LIABILITY PERIOD |  | Approved / Not Approved |  | Signature | Date
Zone Representative (Zone Estate Management & Planning Member):

## 5. HOTO Caveat Logs
HOTO Caveat Logs
Attachments (Logs):
Defence provided Caveats.
Project Issues.
Contract Deliverables Not provided
Project: - |  | 0
Project Location : |  | 0
Building/Assets Description & HOTO Descriptor:
CFI Project Director / PDS Project Manager or any Defence entity project manager: |  | 0
Project Manager Contract Administrator (PMCA):
Contractor:
Project Caveats – Issued by Defence
Caveat ID | Caveat Description | Issued by PMCA/PM (Insert Name) | Date issued (Actual) | Closed by (Name) & Location of Supporting Evidence | Updates/Remarks by PMCA/PM
Project Issues Log – Raised by PMCA /PM, Contractor, EMP Representative or PAS PSS
Issue ID | Issue Description | Raised by (Name & Entity) | Expected Resolution Date | Closed by (Name) & Location of Supporting Evidence | Verifying Person
Incomplete Project Deliverables – Raised by PMCA / PM or Contractor
Deliverable ID | Project Deliverable Not Provided - Description | Raised by (Name & Entity) | Expected Delivery Date | Closed by (Name) & Location of Supporting Evidence | Verifying Person

## 6. Proj Lifecycle Criteria Inst
Project Lifecycle Criteria Instructions
Item | Criteria Note: Cells are linked and Can be edited from tab 2 | Description | Suitable Evidence May Include Note: Cells are linked and Can be edited from tab 2 | Comments | Links
Project Planning & Development Phase |  |  | Achieved by evidence below.
1 | Project start meeting held where key Stakeholders are identified and Project HOTO requirements are discussed and confirmed including:- - Clarification of Project Scope - Provision of Baseline Project Schedule - Access provided to project web based document management systems | Project start meeting held where key HOTO Stakeholders are identified and requirements discussed for Project HOTO Plan & Checklist. Project Stakeholders. The contractor, PMCA / PM, PAS PSS and Zone EMP representatives are to ensure that all applicable stakeholders have been identified, engaged and their responsibilities / ongoing engagement are understood early in the project planning & design phase. The HOTO RACI can assist with this process. Early stakeholder engagement and consideration of applicable HOTO criteria ensures stakeholder input can be quantified in the development of project plans and attendance at project meetings agreed. Depending on the nature of the project the PMCA / PM are to make a considered decision as to which stakeholders are required to be a part of the process. Any doubts about project stakeholders should be referred to DELM for further information and guidance. Where works include JCG managed infrastructure and assets, Log a Job to engage ICTSM (ICT Support Managers) as a stakeholder for the project. Clarify Scope of Works The contractor and PMCA / PM are responsible for engaging stakeholders to clarify and confirm the scope of works for the project and what is expected. The agreed scope of works shall be provided to all identified stakeholders. Project Stakeholders are to consider siting options of the proposal to identify constraints and risks and to inform the design phase. The scope of works should be confirmed before the design contractor procurement process begins. For CFI projects the agreed scope of works are detailed in the approved IBC or DBC. | A copy of the project start meeting minutes. If not addressed in the minutes, also provide a copy of: * List of key project stakeholders and their ongoing role / required meeting requirements. *Acknowledgement that key stakeholders received & agree (where applicable) the project scope of works. *Copy of IBC or DBC authorities page. *Baseline Project Schedule * An email from the PMCA / PM advising data system access arrangements and list of stakeholders provided access .
|  | Access to document Manage Systems. The Objective Work Group Coordinator/s within CFI and DEWPO are responsible for providing all stakeholders, contractor’s etc. access to the objective files / folders required for the project. CFI Projects: Contractors will generally use a web based or commercial document management system (e.g. Aconex) to manage these documents during the project and deliver them to Defence progressively throughout the project. There is no mandatory requirement for PMCA's and Contractor to use Objective. The PMCA is to liaise with the PAS PSS and Zone EMP representative to determine project stakeholders requiring access and apply a suitable file structure for ease of locating the required information. Transfer of project files from the contractor’s commercial document management system into Objective is later facilitated by CFI project officers and/or PMCAs by providing EMP representatives and PAS PSS the respective project documents via DVD / USB. Ideally this should occur in batches that align to project phases (Design, HOTO & DLP) and the end of stages. EWP Projects: Objective is to be used by the PDS to store project documents, applicable estate information deliverables and HOTO information. Exceptions apply where Defence policies and instruction's specify otherwise. i.e. GEMS data (GDLs) to GEMS, Spatial data (including spatial GDL outputs and GIS layers) to the Estate Geospatial System. |  |  | OBJECTIVE: Base Services Contract Operating Instruction for Objective and Defence Information Management
1.1 | Project HOTO Plan and Checklist | The PMCA / PM is responsible for ensuring that the contractor’s handover / takeover (HOTO) plan/s are developed in accordance with the contract T&Cs, HOTO policy and instructions detailed on Defence Intranet, and that key project stakeholders are engaged in the progressive development and acceptance of the plan/s and evidential requirements. i.e. Stakeholders - Zone EMP and Environment & Sustainability (ES) staff, applicable Defence SME and Product Directorates, PAS PSS & PAS Project Data Service. Contractors must use the HOTO Plan & Checklist located on Defence Intranet. The HOTO plan intends to provide explicit detail about applicable HOTO activities, compliance requirements, how criteria will be satisfied and what evidential material and/or documents are to be provided. A HOTO Plan & Checklist template is provided on Defence Intranet for use when developing the HOTO plan/s. Contractor and project stakeholders must refer to the instructions and Project Lifecycle Criteria Instructions within this HOTO Plan & Checklist document for additional guidance about content of the document and how it should be used throughout the project lifecycle. The HOTO Plan & Checklist sets the minimum requirements for ensuring compliance and fitness-for-purpose at completion of works, and an efficient HOTO transition. Therefore the HOTO Plan & Checklist should be regularly reviewed to ensure actions resulting from changes in project conditions and outcomes are agreed and documented. If agreement on the above plans, HOTO criteria and evidential requirements cannot be reached between the PMCA / PM, Defence Representative and Contractor; the issue escalation process detailed in the project contract documents is to be followed and the matter is raised with the applicable accountable authority detailed in the HOTO RACI and project contract. e.g. for CFI projects unresolved issues may be raised in specified project meetings and escalated to PCGs and then for further decision, to the PGBs. Note: Depending on the project type (HC, MC, DSC, D&C or EWP) determination of applicable HOTO plan content and criteria will vary in timing within the project lifecycle . Note: The PMCA / PM (in consultation and EMP & PAS PSS) can determine a draft HOTO plan and checklist with proposed criteria selected (Applicable to the project) for inclusion in tender documents associated with later project phases. i.e. engagement with DSC or HC. | Provision of an agreed HOTO plan & checklist. |  | OBJECTIVE: Base Services Contract Operating Instruction for Objective and Defence Information Management | DPN: Handover and Takeover (HOTO) | DEFENCE.GOV: Handover and Takeover (HOTO)
Project Design Phase
2 | Design initiation start meeting to confirm stakeholders, scope and design requirements. | Throughout the project design phase there may be several meetings and various activities conducted to ensure the required stakeholders are engaged, project scope and deliverables (including approved changes) are understood & agreed; risks and constraints are identified; and plans, designs and drawings are developed to the required standards. Design initiation start meeting. Must be held at the commencement of the design phase. The PMCA / PM are to ensure that all appropriate stakeholders are identified and represented for the meeting. Items that should be addressed at the design start meeting may include but not be limited to: a. All applicable stakeholders and SME for the design phase activities have been identified and engaged. b. Project scope, schedule and deliverables are clearly understood and agreed to by key stakeholders. c. Site risks, constraints, environmental management and renewable energy requirements identified. d. The HOTO Plan & Checklist for the design deliverables is reviewed, acceptance criteria and completion evidence are agreed. e. An Estate Information Provision Plan (EIPP) & Data Provision checklist (DPC) for the supply and management of estate information has been reviewed and agreed. The EIPP should cover provision of GEMS data, estate data extracts, drawings and geo-data etc. f. PMCA / PM arranging Estate Data extracts for all existing infrastructure, buildings and equipment affected by the project works. Requests for these extracts are to be prepared using the Request Estate Data Form, to define the scale and extent of data to be included. g. Ensuring that PAS specialist maintenance advice is provided during the design process. The PAS are able to provide maintenance advice for buildings, infrastructure, plant & equipment and land management requirements. h. Base access arrangements for visitors etc. i. Explain PAS PSS services, clarify notice and return times for estate data and RFIs. Where available PAS are to provide contractors an information pack about PAS PSS services. j. Where a Design includes installation of a renewable energy supply please liaise with DERMS. email: Smart.infrastructure@defence.gov.au k.EGIS Product Report (EPR) and EGIS Advice Register (EAR) creation, storage and usage requirements are understood. Relevant Policy Owners are notified of Project’s EAR Objective location for their future use. Larger and more complex designs generally have design milestones established at 30%, 50% and 90%, with corresponding design review meetings. The contractor and PMCA / PM must ensure applicable stakeholders and SME have been adequately engaged to provide input at agreed project design review milestones and/or meetings. | * Email from PMCA / PM advising that criteria is met and a copy of the minutes are saved in Objective or for CFI, the mandated project information management system. * Copies of design review meeting minutes and/or correspondence from key stakeholders and SMEs acknowledging design input and/or acceptance. |  | DPN: National Spatial Information Management System (NSIMS) | DPN: Estate Governance and Integrity System (EGIS)​​ | OBJECTIVE: EGIS Policy Matrix | DPN: Defence Policy Document Library
2.1 | Estate Information Provision Plan (EIPP) and Data Provision Checklist created and agreed. (Refer Tab 3 DPC & Tab 8 EIPP Template) | Contractor (designer) is required to develop a Estate Information Provision Plan (EIPP) that details what, how, who and when estate data associated with the project will be managed and provided to Defence. The EIPP must cover management and delivery arrangements for all forms of new and changed estate data that is defined by the Estate Register Information Model (ERIM), environmental and estate related registers, project plans, drawings and manuals etc. The EIPP must accord with applicable Defence policies, business rules and manuals to ensure the conditions of the contract are met and provision & acceptance of quality data is achieved at the required project phases. When developing the EIPP and Data Provision Checklist (DPC) , contractors must liaise with PMCA / PM and PAS PSS to ensure associated processes are understood and planned data supply and verification schedules can be achieved. Refer to the EIPP Template (tab 8) for further information about EIPP requirements. Refer to the Data Provision Checklist (tab 3) and data provision checklist Inst (tab 7) in this HOTO Plan and checklist document for further information about DPC requirements. Note: Design services contractors only need to complete an EIPP and select applicable DPC criteria listed in the design phase. | Provide copy of agreed EIPP and DPC. |  | DPN: Estate Data Information | OBJECTIVE: Data Dictionary
2.2 | Compliant Design Where required:- * approved performance solutions IAW Building Works Manual (BWM) * approved Dispensation IAW the Building Works Manual (BWM). | Design approval is the responsibility of the design team where all designs must comply with all applicable Codes, Standards and Defence policies etc. Defence engages the project contractor to provide compliant estate items generally without additional approval from Defence, however, delivery of estate items that do not satisfy Defence policy requirements will need to be approved via a dispensation or performance solution requests. The Contractor must seek approval for dispensation or performance solutions from the appropriate authority as identified in the Estate Engineering Policy which includes the Building Works Manual (BWM). The Estate Engineering Policy web site will provide additional links for specialist engineering advice, or a request can be forwarded from the contractor and/or PMCA / PM to to the relevant DEEP Section. All Project to Policy Owner(s) interactions shall be recorded in the EPR. The design contractor is to review the scope of works and confirm if it is sufficient to facilitate a Certificate of Completion being issued by the building surveyor for the project. Where changes to an existing building or structure are considered as exempt works under the BWM, the delivered works may not require a Certificate of Completion to be provided. In these circumstances a letter from the building surveyor is required. To demonstrate compliance in design, designers are to certify that designs meet all applicable legislative, standards and Defence policy requirements for the systems and services relevant to the project. These may include: a. plant and equipment; b. essential safety systems; c. electrical services, d. where work is required to the Defence Electrical Network or the incoming base electricity supply, an appropriate Electrical Development Plan shall be developed in accordance with the MIEE. Note: the design must consider concurrent and future planned works and their utilisation of spare capacity for the incoming base electrical supply. e. mechanical & hydraulic services; f. fire & smoke protection & management; g. fuel storage and distribution facilities and equipment; h. hazardous areas, include explosive ordnance (EO) and hazardous chemical storage; i. security systems, Sensitive Compartmented Information Facilities (SCIF), magazines, armouries, supervisory and security Zones 2-5; and j. ICT and Voice Services. k. Performance Solutions in accordance with BWM. l. identify Critical Equipment and Critical Spares | Where applicable and in accordance with Estate Engineering Policy Provide: *Copies of designer certifications for all applicable aspects. *Where designs require other SME endorsement like FSB, EO and JCG; provide a copy of SME certification notice. *Copy of the approved performance solution prior to the issue of a building approval. The "Request for Performance Solution Template" can be found under the templates link on the Engineering Policy - Building Works page. *Copy of the approved dispensation request prior to issue of a building approval. The "Request for Dispensation Template" via the Estate Engineering Policy page. *Copy of Electrical Development Plan where Electrical Network or Base Supply works have been undertaken. |  | DPN: Estate Engineering Policy | DPN: Electrical Engineering | DPN: Building Works | DPN Mechanical Engineering | OBJECTIVE: EGIS Product Report
|  | Performance Solutions. The requirements of the NCC are met by demonstrating compliance with the performance requirements of the NCC. This is achieved by either developing a performance solution, a deemed-to-satisfy (DTS) solution and / or a combination of performance solutions and DTS solutions. Where a departure from the DTS provisions of the NCC is proposed or there are no applicable DTS provisions , a performance solution is required to demonstrate compliance with the relevant performance requirements. The performance solution shall detail the methodology applied to meet the performance requirements of the NCC – e.g. clause A2.2(2) of the NCC (volume one). The delivery authority or their delegated representative shall forward a formal request for agreement of any performance solution to the Director of Estate Engineering Policy via the DEEP.Advice@defence.gov.au email address using the approved template. Further guidance can be found in the BWM (Chapter 8) and the Guidelines for Certification, Performance Solutions and Dispensations. Dispensations. Defence may have specific policy requirements that are in addition to the NCC. The requirements of the Defence policy are met by demonstrating conformance with the provisions of the applicable requirements. Where a non-conformance to a Defence policy is sought, a dispensation is required. The delivery authority or their delegated representative shall forward a formal request for dispensation to the DEEP.Advice@defence.gov.au email address for Assistant Secretary Environment & Engineering (ASEE) approval. Requests for Defence approval of dispensations must use the approved template ‘Request for dispensation’. A copy of any approved requests will be returned to the delivery authority. In the event of non-agreement, formal advice outlining the reasoning will be provided from the delegated representative to the delivery authority. Further guidance can be found in the BWM (Chapter 8) and the Guidelines for Certification, Performance Solutions and Dispensations. Note: Where performance solutions and dispensations are proposed in the same building, a combined ‘Request for performance solution and dispensation’ form may be used where permitted by the policy owner. |  |  | DPN: Fire Safety | OBJECTIVE TEMPLATE: Request for Performance solution and Dispensation | OBJECTIVE: Building Works Manual | DPN: Bushfire Planning Management
[5 empty] | OBJECTIVE: Building works Templates | DPN: Estate Governance and Integrity System (EGIS)​​ | OBJECTIVE: Guidelines for Certification, Performance Solutions and Dispensations
2.3 | Design considerations:- * Safety in design conducted and findings accepted * MFPE Design requirements for Bushfire Prone Areas. *Smart Infrastructure in Design * Security in Design | Safety in Design. All construction works must undergo a “Safety in Design” review to determine any hazards that may be created by the design of the intended works and design them out (eliminate) or where they cannot be eliminated reduce so far as reasonably practicable. EGIS and the Code of Practice for Safe Design of Structures provides details for understanding and conducting a Hazard in Design. MFPE Design Requirements. Chapter 10 of the MFPE details the Defence risk assessment and mitigation requirements for bushfire prone areas. Designers are to liaise with the Base Manager (BM) and Zone ESO to obtain existing bushfire management plans and information to inform risk assessments for new designs. Further information on Bushfire Environmental Factor Records can be found under the reference guides on the GEMS Gateway. Review of Design Hazards. designer adequately considers reasonably foreseeable hazards that may occur as the structure is built, commissioned, used, maintained, refurbished or modified and are eliminated or reduced to as low as reasonably practicable. Deciding what is ‘reasonably practicable’ requires taking into account and weighing up all relevant matters including: a. the likelihood of the hazard or the risk occurring; b. the degree of harm that might result from the hazard or the risk; c. knowledge about the hazard or risk, and ways of eliminating or minimising the risk; d. the availability and suitability of ways to eliminate or minimise the risk; and e. after assessing the extent of the risk and the available ways of eliminating or minimising the risk, the cost associated with eliminating or minimising the risk, including whether the cost is grossly disproportionate to the risk. At times this may include Radiation or radioactive equipment, The Security and Estate Group Radiation Safety Management Program (SEG RSMP) details how radiation is managed within SEG. The program aims to provide necessary information for managing all instances of using radioactive materials, for example X-Ray Baggage Machines, by SEG workers. It also provides guidance on our responsibilities in managing radioactive materials on behalf of Defence. Security in Design. If there are any security requirements and/or implications in a facility, DS&VS should be contacted prior to the design phase to ensure Defence requirements are met in designs. Complex projects with security zones 2-5 or armouries should complete a security risk assessment to guide and inform the design. A SCEC Consultant should be engaged for any project with security zones 3-5 who represents the interests of the Commonwealth. | Where applicable and in accordance with EGIS, BWM & MFPE provide: *Design review documentation identifying any hazards requiring treatment, i.e. a register and associated risk management measures. *Email demonstrating DS&VS engagement and where applicable, details of SCEC engaged consultant. *Email demonstrating Base Manager and Zone ESO engagement for risk assessment and treatment designs (for example through APZs). *Copy of completed Smart Infrastructure Checklist provided in Smarti Manual. |  | OBJECTIVE: Manual of Fire Protection Engineering | OBJECTIVE: Defence Radiation Safety Manual (DRSM) | OBJECTIVE: Radiation Safety Management Program | OBJECTIVE: National Sub-meter Program Requirements
|  | Smart Infrastructure in Design. Defence requires all new design and construction projects to continuously improve the efficiency, effectiveness and sustainability of the Defence estate. Smart Infrastructure defines the Defence requirements and reporting obligations for design and construction covering energy, water, waste, pollution prevention, and smart procurement. Smart Infrastructure consists of two parts: a. A Manual that outlines Ecologically Sustainable Development (ESD) and Whole of-Life (WOL) requirements for each project, covering: design, construction and associated reporting. b. A plan and checklist that Guidance see Defence Intranet link. It is the designer's responsibility to ensure smart infrastructure principles are implemented into all designs for works specified. |  |  | DPN: Sustainability | DPN: Smart Infrastructure | OBJECTIVE: Smart Infrastructure Handbook (Smarti)
2.4 | PAS input to design, whole-of-life and DLP maintenance requirements. | The PMCA / PM is to ensure that PAS/ Post DLP Maintenace Agent specialist design, whole-of-life and DLP maintenance advice is provided during the design process to maximise efficient operability and optimal maintainability. The PAS are able to provide maintenance advice for buildings, infrastructure, plant & equipment, and land management requirements. PAS PSS is responsible for inviting and coordinating applicable PAS specialist attendees and or MSP's where applicable to design review meetings. PAS PSS and PAS failure to meet this requirement should be raised with Director Estate & Land Management (DELM) for resolution. Note: The purpose of PAS review of designs is not to check / certify a design’s compliance with applicable standards and/or codes of practice. PAS advice is to inform designers of the requirements for optimal and efficient solutions for ongoing maintenance practices. PAS have a 2 week maximum turn-around time for review and comment. By the 90% design milestone, PAS/ and PMCA / PM are to establish the agreed maintenance arrangements and responsibilities for DLP. For example, is maintenance to be conducted by the PAS, contractor or a mix of both. Determining this arrangement will enable the PMCA / PM to specify arrangements in tender documents when engaging the construction contractor and enable PAS to prepare a seamless transition at the commencement of DLP. | A copy of invitation correspondence (email or other) issued to PAS and PAS confirmation of attendance and/or provision of feedback.
2.5 | Building Contribution Factor for new built facilities, new leases or where the building work changes the CF of an existing building. | During the early design phase of a project the proposed building must be categorised in accordance with its contribution to capability. This process is completed in consultation with the applicable Capability Manager. The outcome of the assessment is expressed as a Contribution Factor (CF). CF definitions can be found in Section 2 of the Guidelines-for-Contribution-Factor-forms and Chapter 5 of the BWM. The Building Contribution Factor Form is used to document the outcome of the assessment process and the completed form is to be recorded in GEMS. The CF form is found at Annex 5A of the BWM. This process is only required for new buildings, new leases or where the building work changes the CF of an existing building. BMs are the approval authority for common areas / facilities and Capability Managers (or their delegate) are the approval authority for their facilities. Note: The CF of a building may result in additional Defence asset protection requirements to those specified in the NCC. Note: This must be commented early in the design phase to inform Designers about the design requirements. | Email from Capability Manager (ASEP or delegate) where applicable to indicate that the Building Contribution Factor Form is provided for file and the form has been submitted. Email from Capability Manager (ASEP or delegate) to indicate that no change is required (for existing facility). If a change is required, a copy of the Building Contribution Factor Form is provided for file and BM / Capability Manager (or delegate) advise the form has been submitted or copy of DBC approval page. |  | OBJECTIVE: Building Works Manual | OBJECTIVE: Building Contribution Factor Assessment Form | DPN: Estate Appraisal | OBJECTIVE: Guidelines for Contribution Factor Forms
2.6 | Site Selection Board Completed and Approved | Prior to constructing a facility on Defence owned or leased land, siting approval is to be gained via a Site Selection process. The process is designed to ensure the facility is located to the best advantage for its intended purpose and does not create conflict with future works or surrounding infrastructure or their intended purpose. Initially this process is a high level, desktop review where Base and Zone EMP staff are engaged by the project at pre-design to check and confirm that the potential project site/s are not already selected for other facilities, works and/or have environmental restrictions that inhibit the project works. The complete site selection process (regional review or full review) will be conducted in the design phase. Site Selection recommendations is a responsibility of the Site Selection Board which comprise of Defence members with specific knowledge and interest in the location selected for the new infrastructure. Contractors are responsible to review site selection documents and approval requirements to ensure the planned works comply with the approved site selection outcome. For CFI projects, DBC approval will not occur without completion of a site selection assessment. The Site Selection Page on Defence Intranet provides the processes, templates and guidance to achieve site selection. | A copy of the site selection recommendation(s) approved by the Delegate. For CFI project - a copy of the IBC or DBC approvals page. |  | DPN: Estate Site Selection | OBJECTIVE: Site Selection Handbook
2.7 | PAS Information Pack | The PAS PSS is to provide an information pack to the PMCA / PM and contractor explaining the assistance to be provided. These may include: a. PSS Development Delivery Model; b. PSS Useful Information - Managing Estate Data; c. PSS Project start-up information; d. RFI Template; e. escort request form; f. Label Request Form; g. PSS HOTO Supporting Information; h. HOTO Flowchart; and i. how to lodge a request for works or support. j. PAS Project Data Service roles | An email from the PDS or PMCA to confirm receipt of PAS Information pack for inclusion into HC / MEWC tenders or copy of minutes where receipt has been noted.
2.8 | Data Provision Checklist Actions & Deliverables have been completed and verified for Design Phase | Where a Data Provision Checklist (DPC) is established and agreed at the commencement of the design phase, DPC actions and deliverables are to be regularly reviewed and completed as early as practical. This criteria is met once the agreed design phase actions and deliverables have been completed. Refer to the data provision checklist and data provision checklist Inst tabs in the HOTO Plan and Checklist document for further information about DPC requirements. | Design Phase of the Data Provision Checklist Completed
Pre-Mobilisation |  |  | Achieved by evidence below.
3 | Pre-mobilisation start meeting held with stakeholders, scope of works and design confirmed and Project commissioning & HOTO Plan & Checklist, DLP outline maintenance plan, training requirements identified and delivery plan all agreed by HOTO key stakeholders | In preparation for the construction phase there are several important requirements that contractors and project stakeholders must complete before contractors can access and mobilise on the Defence estate. These requirements must be discussed and agreed upon at a pre-construction start meeting. The PMCA / PM are to ensure that all applicable stakeholders are represented at the meeting and HOTO Plan & Checklist pre-mobilisation items are adequately covered by the meeting agenda. Topics that should be addressed at the start meeting may include but not be limited to: a. All applicable stakeholders and SME for the construction phase have been identified and engaged. b. Project scope of works, schedule and deliverables are clearly understood and agreed by key stakeholders. c. The building surveyor must be present at the pre-construction meeting to provide advice in relation to the Building Approval (BA) (once construction is complete). Building Approval will only be issued by the building surveyor when the requirements of MFPE paragraph 3.16 have been met. d. A HOTO Plan & Checklist covering the construction and to the end of DLP phases are reviewed, acceptance criteria and completion evidence are agreed and documented in the HOTO plan. This will include from the Contractor Rep a draft DLP workflow a plan. e. A Data Provision Checklist (DPC) for the supply and management of estate information has been reviewed and agreed. The plan should cover the scheduled provision of estate information, data extracts, plans, drawings, geo-data, building and O&MMs, etc. f. Schedules and plans for commissioning and operator & maintainer training. g. Site Management and control plans. h. Completion of dilapidation surveys and demolition plans. i. Environmental management requirements and approvals. j. Connection & dis-connection of energy and water services. Raise AE879, refer to checklist criteria 5.32 for more details. k. Agreed the DLP outline maintenance plan (strategy and approach) with PAS for the project elements and PAS are to advise requirements for the subsequent DLP maintenance plan to be later developed. The DLP plan must consider what maintenance and support is and could be provided by PAS during DLP. For more details refer to criteria 2.4 for both CFI and EWP projects. l. Confirm if a property licence is required for building occupation after HOTO completion. EMP are to notify the Out-posted Property Officer (OPO) if it is thought that a licencing requirement will apply and the OPO is to facilitate any following requirements and/or actions. | Copy of meeting minutes. Copy of agreed HOTO Plan & Checklist. If not recorded in the meeting minutes, a copy of the agreed (with PAS) DLP outline maintenance plan, where applicable. |  | OBJECTIVE: Manual of Fire Protection Engineering | DPN: HOTO
Training Requirements. In consultation with the PAS PSS and RU, the contractor is to review the works being delivered and determine if / what training (and inductions) is required to prepare operators and maintainers to safely and correctly operate and maintain the infrastructure being installed. The identified training is to be agreed between all stakeholders in regards to the: a. type and complexity of training required; b. number of staff to be trained; c. style of training i.e.: on the job, classroom, Train the Trainer or a combination of all; d. competency level to be achieved; and e. what competency / qualification will be provided / awarded to the participants? It should also be identified what qualifications are required to operate and/or maintain the delivered infrastructure which will not be provided by the project to allow time for these qualifications to be gained prior to HOTO. At this stage of the project, only general requirements need to be discussed and recorded in the meeting minutes.
DLP Maintenance Plan. For EWP projects that involve refurbishment / repurposing facilities and/or replacement of systems and/or sub-components with new assets, the PAS should continue to be the maintenance provider at the end of construction. The PAS will need to develop their maintenance plan, with contractor input / assistance (on maintenance schedules & tasks associated with the project delivered items), and incorporate new warranty provisions (without voiding those manufacturer warranties) for new and refurbished items for the first 12 month period (nominal DLP). Determination of the DLP maintenance responsibility is to occur at the end of the design phase in a 'project maintenance meeting' held between PDS and PAS. This will inform tender documents for the construction phase. Where a complete new building / facility is constructed and/or refurbishment delivered via the CFI program, the contractor will be responsible for DLP maintenance. If the Contractor desires to engage the PAS to conduct DLP maintenance, that is an arrangement to be formally negotiated and established between the Contractor and PAS. For either option, the Contractor and PAS must meet in the pre-construction planning period to confirm and agree DLP maintenance arrangements before construction commences. The Contractor is to commence by providing PAS with a DLP outline maintenance plan for PAS review and input into the plan’s development during the construction phase. The DLP maintenance plan is to be finalised at a time prior to HOTO as agreed with the PMCA / PM and PAS, and the BSSC prepared to respond in support, from the completion of HOTO. To be effective, the estate information that the plan relies on, which includes warranty information, must be in GEMS and the O&MMs. The plan should outline: a. confirmation that the applicable CCPs have been approved for post DLP work; b. PAS responsibilities for responsive, scheduled and performance maintenance as per the required maintenance plans; c. details of maintenance to be performed by the contractor representative; d. procedures for rectifying delivery contractor defects; e. procedures for manufacturer and collateral warranty claims; and f. roles and responsibilities for formally completing the DLP.
3.1 | Estate Information Provision Plan (EIPP) and Data Provision Checklist created and agreed. (Refer Tab 3 DPC & Tab 8 EIPP Template) | Contractors (Head Contractor - HC) are required to develop a Estate Information Provision Plan (EIPP) that details what, how and when estate data associated with the project will be managed and provided to Defence. The EIPP must cover management and delivery arrangements for all forms of new and changed estate data that is defined by the Estate Register Information Model (ERIM), environmental and estate related registers, project plans, drawings and manuals etc. The EIPP must accord with applicable Defence policies, business rules and manuals to ensure the conditions of the contract are met and provision & acceptance of quality data is achieved at the required project phases. When developing the EIPP and Data Provision Checklist (DPC) , contractors must liaise with PMCA / PM and PAS PSS to ensure associated processes are understood and planned data supply and verification schedules can be achieved. Unless otherwise agreed and in accordance with contractor’s agreed EIPP, estate information should be provided as early as possible before the 90% construction or 28 day notice point to provide sufficient time for PAS PSS to check and upload GDL data by HOTO. This includes but is not limited to GDLs for buildings, equipment, asbestos, contaminated sites and hazards; “draft” manuals, as-constructed drawings, plan and geo-referenced information etc. For small and short duration EWP projects it is recognised that the provision of all estate information at 90% construction or 28 day notice of completion is not achievable. In these circumstances the contractor is to seek agreement with the PMCA / PM, PAS PSS and Zone EMP for the supply of all estate information at a time closer to HOTO. Typically this may be 7 days prior to HOTO. The agreed estate information delivery schedule is to be documented in the EIPP. Refer to the Data Provision Checklist (tab 3) and data provision checklist Inst tabs in this HOTO Plan and Checklist document for further information about DPC requirements. Note: HCs only need to complete an EIPP and select applicable DPC criteria listed in the Construction, HOTO and DLP phases. | Copy of agreed Estate Information Provision Plan (EIPP) and Data Provision Checklist (DPC).
3.2 | Site Management Plan/s. | Depending on the project scope & activities a Site Management & control plans are to include the following where applicable:- 1. Base and Site Access methods with diagrams. 2. Site and/or construction security 3. Traffic Management 4. Confirmation of site ownership on occupation 5. Environmental Management 6. WHS - Site Safety, Induction Briefs, Incident management procedures and/or Permit system and template. The PMCA / PM are to ensure that Defence and Base requirements are incorporated in the Contractor's plans. Contractors must liaise with the base staff in the development and agreement of all related plans. Site Preparation. The contractor must engage with the BM, PAS Manager and RU to plan and review project site specific information to identify and agree to the site required for the proposed works. Management plans, base instructions and sites and services that will be affected or isolated are to be provided to the affected RU and service providers (internal and external). The external service providers could include utilities, Telstra and nbn.co. Where plans cannot be agreed the project escalation process should be invoked. To facilitate the planning and review, contractors are to provide applicable documents and drawings depicting the areas to be affected and occupied for the purpose of the construction, commissioning and HOTO phases. This includes areas required for contractor’s temporary office accommodation, contractor parking, decanting and storage of materials and waste etc. Site access and security. A risk based security plan is developed prior to any works commencing. The plan should recognise existing security risks on a base with a view to limiting impact of the construction activity. Options such as separate access points, additional guarding, workforce ID and targeted security clearances are some examples that have been utilised. The Security Plan will need to cover the security of the construction, especially if the facility under construction or refurbishment will house highly classified or sensitive activities, assets or information. Traffic Management. Obtain input from the BM, RU and/or PAS manager to prepare traffic management plans for the base and affected site(s). The BM will ensure updates are sent to all Base residents/workers to advise of the possible disruptions. | Evidence to include copy of correspondence to Base & PAS of agreed Site Management Plan/s.
Site Safety and Inductions. All contractors shall have their company specific site inductions for the project / task and any work site or designated property that will be controlled by the contractor. The contractor is also to ensure that specific site inductions (incorporating all Defence and Base requirements), has been provided to all staff and that attendance at the inductions is registered. Includes Airside Awareness for Bases with operational airfields. Utility Isolations. The contractor is to develop a utilities isolation plan / procedure in conjunction with the PAS, BM and RU. The affected RU and service providers are to be advised as per base communications arrangements. The BM can then create a notification for the Base to advise of the isolations. Communication of isolations and notice of disruptions should make use of the Base Information Circular or email systems. The PAS is Defence’s High Voltage Controller for all electrical systems within Defence estate. Where electrical systems are to be isolated from the mains power to allow works to be conducted by a project, the HV Controller is to place a tag on the isolation breaker / terminal. Power is not to be re-energised until suitable evidence has been provided to the HV Controller by the project that all electrical works are compliant and have been tested as correct. The HV Controller is to then provide the project with approval to re-energise the electrical system. Permit System. Where applicable the contractor is to implement and operate a permit system that is compliant with WHS Act 2011 and applicable regulation and codes of practice for all high risk tasks. For permits involving Base electrical, water and or sewerage systems the PAS must be integrated into their permit system and approval process. The PAS Network Controller must be engaged and perform part of the approval process for the electrical network. A Site Safety Management Plan (SSMP). A SSMP is to define how WHS is managed by the Contractor and other duty holders at shared workspaces. Under an SSMP, all parties shall be satisfied that the agreed arrangements are sufficient for all duty holders to discharge their WHS duties. The identified responsible person is to develop a site specific SSMP and submit to the PMCA / PM for review and confirmation that it meets requirements of the contract and WHS Act 2011. The SSMP is to include the roles and responsibilities and the incident reporting procedure to ensure Defence complies with Comcare reporting requirements. Incident management procedures must cover where applicable: Asbestos, Hazardous Chemicals, and Method of Works Plan for Airfield activities, etc.
3.3 | Dilapidation Surveys | Dilapidation Surveys The contractor is responsible to provide the PMCA / PM, PAS PSS & EMP a copy of the dilapidation survey and any other supporting evidence of the condition of facility and estate items prior to works commencing. The survey may include: a. condition of the estate items prior to works commencing; b. items to be demolished; c. items to be salvaged; and d. items to be disposed. The dilapidation survey is to be reviewed & agreed by PAS PSS prior to commencement of physical works. NOTE: The CFI finance links provided in column F & G are internal only, external links are not available on Defence.gov.au | PMCA / PM email notification of receipt of dilapidation survey.
3.4 | Notification of Demolition | Notification of Demolitions The Notification of Demolition or Disposal Form (available upon request from DFG Asset Accounting Team) is to be completed by the contractor and submitted following the process: a. The Notification of Demolition or Disposal Form must be submitted to the local Defence Finance Group (DFG), Regional Asset Accounting (RAA) section to have the correct Value (Net Book Value) and ROMAN Asset number provided from ROMAN (Fixed Asset Register) for each item where applicable. The RAA section will also provide advice regarding other assets that may be on the Fixed Asset Register that could be involved in, or disposed of, or enhanced by the Project. b. The Asset Accounting Group Mailbox is dsgbsm@defence.gov.au c. The RAA section will return the form to the PMCA / PM. d. The contractor and PMCA / PM must ensure the form is signed by the applicable delegate in accordance with Accountable Authority Instruction 8 Annex C before submitting the form to Directorate of General Asset Accounting (DGAA) via their Group Mailbox dsgbsm@defence.gov.au for processing in ROMAN. The Notification of Demolition or Disposal Form must also contain the proposed asset disposal date(s). e. Following the physical Disposal and/or Demolition of the asset(s) the actual date of this action must be recorded on the original Notification of Demolition or Disposal Form and sent to DGAA for completion of the final ROMAN disposal transactions. Pursuant to the PGPA Act, the Notification of Disposal Form must be approved by the delegate prior to demolition or disposal of an asset (building, infrastructure or OP&E). A copy of Demolitions notification must be provided to the PAS to enable them to plan for the deactivation of services. All buildings nominated for disposal must comply with the provisions of the MFPE until they are demolished. For disposal or demolition of facilities and equipment that have a radiation source, refer to HOTO criteria 5.7 Instructions and links for move information | A copy of the email submission of Notification of Demolition form and provision to PAS PSS. |  | dsgbsm@defence.gov.au | Section 8 - Defence Accounting Policy Framework | DPN: CFI Templates and Resources | OBJECTIVE: Asset Demolition/ Disposal Notification Minute Template | OBJECTIVE: CFI Financial Management Templates
3.5 | Asset Rollout Notification form Prepared & Submitted (Asset Valuation) for all new or refurbished facilities. | An Asset Rollout Notification Form is to be submitted where the applicable capitalisation thresholds are met: Building and infrastructure >$100K Other Plant and Equipment (OP&E) >$10K.The identified Responsible Person appointed by the PMCA / PM is responsible for preparing and submitting the Asset Rollout Notification Form. Preparation of the Asset rollout notification form should commence as early as practical in the construction phase to identify assets under construction. The Asset Rollout pack (available upon request from DFG Asset Accounting Team) contains guidance to completing the Asset Rollout Notification Form and identifies the required submission stages of the project. Fully completed rollout packs, with accompanying signed notification forms and NOCs are to be emailed to: For CFI projects: ID Finance group mailbox, ID Finance - MCF idfinance-mcf@resources.defence.gov.au For EWP & Other: AUC Correspondence auc.correspondence@defence.gov.au Note: Asset Rollout Notification Forms are required for all CFI & EWP project where works completed increased the asset value above respective financial threshold | A copy of the Asset Rollout Notification email submission. |  | dsgbsm@defence.gov.au | OBJECTIVE: Asset Roll Out/ Asset Roll Out Enhancement Pack Template | DRN: Accounting Policies | DRN: Assets Under Construction​ | DRN- Defence Project Accounting Manual
3.6 | Environmental Clearance Certificate (ECC - form AB081) submitted and approved by Zone ESO, including an Environmental Management Plan (EMP) where relevant. | ECC form AB081 is required for conducting projects / activities on Defence property or leased sites where the project or activity: a. is beyond the scope of approved Range Safety Officers (RSO), Standing Instructions (SI), Standard Operating Procedures (SOP) or other documented systems and associated instructions; b. is undertaken on the Defence estate (e.g. construction or maintenance) by external agencies; c. has any likelihood of causing significant environmental impact in the absence of strict controls; and d. is a controlled action under the EPBC Act (the ECC will be issued to ensure the conditions of approval are communicated, understood and complied with). Environmental impact assessment is an integral part of the project planning, development and delivery process for all Defence actions and projects. Defence actions are broadly summarised as all the activities, projects, developments, demolitions, exercises, trials, undertakings and introductions of new capability undertaken by or on behalf of Defence. An ECC is the final Defence environmental approval. It is informed by an Environmental Assessment Report (EAR) where applicable and imposes site specific conditions and safeguards to ensure so far as reasonably practical, that environmental impacts, including contamination, are removed or minimised. Once an ECC is issued, the activity for which approval has been sought may commence. An ECC is only for activities detailed during the assessment phase. If there are any changes to the scope of the action, or if previously unidentified issues arise, a revised or additional ECC will be required. An ECC can also be issued to a staged development. This provides the proponent and the contractor some certainty that the overall concept of a project has been approved via the EAR but full details of each stage need not be given when the first stage ECC is applied for. The ECC is to be raised by the contractor and submitted to the Zone ESO and include the following: a. Requirements of/for an incident report. An incident report is only required if an environmental incident occurs during the project works. Results, resolution and any mitigation implemented against the incident are to be reported within the ECC. b. Maintenance schedule for Landscaping, Fauna ‘offsets’ – nest boxes, Fauna friendly fencing. c. Vegetation offsets and Population control devices. d. Method of bird control including but not limited to physical and visual deterrents, sonic devices, trained birds of prey, chemicals, contraceptives, and active barriers. e. Native plants of like providence for low or no irrigation landscaping. f. Ensure resource intensity e.g. energy / water consumption per m2 is as per the design energy modelling. | A copy of the approved ECC by the Zone ESO. |  | DPN: Environmental Impact Assessment and Approval | DPN: Environm​ent and Heritage | DPN: Contamination | OBJECTIVE: Environmental Clearance Certificate (ECC) template | DEFENCE.GOV: Contamination Management
Construction |  |  | Achieved by evidence below.
4 | PAS has established maintenance and support (including relevant MSP's or Other Maintenance Agent) by: CFI Projects - 28 day notice of completion, All other projects by 90% construction. | PAS PSS are to confirm that they have received sufficient information i.e. accurate shell records are created in GEMS, DLP outline maintenance plan, O&MMs etc.; and have arrangements in place for PAS/Maintenance agent and MSPs to provide the required operational and maintenance support at the time of facility handover and occupation / use. Where the receipt and processing of GEMS data has been completed, PAS must quickly progress development and submission of CCPs to replace extant support and maintenance arrangements. | PAS email correspondence confirming that the required PAS and MSP operational and maintenance support is ready to proceed at facility handover and occupation / use. |  | OBJECTIVE: GDL Guidance Documents
4.1 | Contractor to provide a Commissioning and Training Plan | All projects (where applicable) shall have a Commissioning and Handover Plan that includes appropriate Inspection & Test Plan (ITP) for the commissioning of all equipment and systems. Each ITP must have at least one Inspection & Test Result (ITR), however, may have multiple where individual testing is required. ITPs may form part of the contractor's Commissioning Plan. The results are to be recorded and form part of the Commissioning and Handover documentation. Where operator and/or maintainer training is required, a training plan and schedule must be developed where suitable notice and training material is provided to enable attendance and attainment of required competencies. The training plan must specify if/when components of training will be conducted during commissioning activities. When developing commissioning plans, ITPs and training plans; Contractors must liaise with PAS PSS to determine where PAS staff and/or maintenance representative need to be involved for the purpose of learning, training, isolations / connections and other applicable controls. Note: PAS Support for this criteria is not to approve or reject ITP and commissioning plans, it just relates to agreed consultation and inclusion where applicable | PAS email correspondence confirming that they have reviewed and support applicable Commissioning, ITP and training plans.
4.2 | Data Provision Checklist Actions & Deliverables have been completed and verified for the Construction Phase. | Where a Data Provision Checklist (DPC) is established and agreed at the commencement of the construction phase, DPC actions and deliverables are to be regularly reviewed and completed as early as practical. This criteria is met once the agreed construction phase actions and deliverables have been completed. Refer to the PDC and DPC Inst tabs in the HOTO Plan and checklist document for further information about DPC requirements. The contractor is responsible for the accuracy, completeness and timeliness of all estate information created or amended by the project. The contract is also responsible to develop Estate Information Provision Plan (EIPP) & DPC that outlines how and when all GDL will be provided to PAS for validation by 90% construction or 28 days prior to notice of completion (as applicable and agreed). | Construction Phase of the Data Provision Checklist Completed
Commissioning
4.3 | Approval from the Defence Electrical Operating Authority (Network Controller) prior to de-energising or energising the electrical infrastructure network | Department of Defence as the owner and user of electrical systems on its establishments is responsible for their operation. Defence vests the responsibility for technical control and operational safety for the Base electrical distribution system with the Defence Electrical Operating Authority (EOA) engaged as part of the Base Services, PAS Contract. The Defence EOA appoints a Network Controller who is the authority responsible for the operation of the Defence distribution system. The Electrical Operating Authority is responsible for;- a. Documenting operating Procedures for the electrical distribution system; b. Configuration and operation of the electrical distribution system at all times; c. Regulating access to the electrical distribution system; d. Appointment and authorisation of personnel required to access, operate or to work upon the electrical distribution system; e. Ensure the safety of all personnel required to access, work upon or work in close proximity tot he Defence electrical distribution system; f. The continuity of supply from the electrical distribution system g. Maintaining adequate documentation of the Defence electrical distribution system; h. Monitoring the condition. status and loads within Defence electrical distribution system; i. Accepting, connecting and energising all works to the electrical distribution system infrastructure; j. Ensuring new works, upgrades or augmentations to the electrical distribution systems are i accordance with the MIEE; k. the safety of and maintenance of the plant and equipment in accordance with Base Services contract requirements and all applicable legislation and regulations. Where a project intends to alter the existing electrical system and / or network, the Network Controller must approve any additions or alterations to the electrical systems they manage. Where a network upgrade is delivered by a project, the project must engage the Base Network Controller who will assist with communicating with the External Supply Authority. Note: the Network Controller approval may be in the form of an email communication or commissioning release as determine by the PAS Electrical Safety Management Plan. | Authority to connect or disconnect to or from the electrical distribution system approved by the Network Controller. |  | DPN: Electrical Engineering
Typically, the following documents would be required as the minimum:- • Approval in writing from the supply authority (supply upgrades only) • MIEE construction stage sign off (supply upgrade or alter Defence HV network only) • regulatory certificate of compliance (Note, this may trigger an inspection by the supply authority. The operating protocol or EISMP for the site will dictate when and if the supply authority needs to be consulted on an installation) • all system schematics and drawings, and where appropriate, any additional reports requested by the EOA, such as Earthing / Protection Reports and / or load studies requested by the EOA have been provided in hard and soft copy format. • EISMP commissioning release (Network Controller) (supply upgrade or alter Defence HV/LV Network). Note: The Defence Electrical Operating Authority / Network Controller has the right to refuse any connection or commissioning of any alterations or new works to the Defence electrical distribution system where in their opinion it could compromise safety and or the operational integrity of the Defence electrical distribution system or where the designer or contractor have not satisfactorily demonstrated full compliance with the appropriate regulations and Defence policy. Note: These requirements are additional to and do not negate the requirement for contractors to liaise with and obtain approvals from the relevant state electrical network authority, where applicable and required by local legislation and regulations. The EOA must be kept informed of any such approvals or communications.
4.4 | Pre-commissioning approvals and notifications completed IAW agreed contractor’s commissioning and HOTO Plan & Checklist | The contractor’s commissioning plan must detail the required notifications and provisions made with the PAS and Base Management personnel. Typical requirements may include but not limited to: activation of HV networks, fire detection / alarm / suppression systems, security systems; and activities that may interrupt or affect Base operational and training activities. There may be circumstances where approvals from Defence Technical Authorities and/or network controllers are required before operation and facilitating commissioning. These include but are not limited to: * For any Defence Fuel Installation (DFI) approval from Fuel Services Branch (FSB) must be obtaining before first energising and operating associated plant and equipment for the purpose of testing and commissioning. * The PAS is Defence’s High Voltage Controller for all electrical systems within Defence estate. Where electrical systems are to be isolated from the mains power to allow works to be conducted by a project, the HV Controller is to place a tag on the isolation breaker / terminal. Power is not to be re-energised until suitable evidence has been provided to the HV Controller by the project that all electrical works are compliant and have been tested as correct. The HV Controller is to then provide the project with approval to re-energise the electrical system. * The PAS is Defence's utility network manager for potable water, fire, sewerage and security systems. Where new installations are connecting to existing networks / systems, the commissioning plan must detail where PAS pre-commissioning approvals are required. * EO Branch are the certification authority for Defence EO facilities. | Copy of Email notification from applicable Technical authority advising approval to proceed with commissioning.
4.5 | Training and / or “train-the-trainer” training provided by the contractor on all facility systems for the operators and maintainers | Training. Where applicable, the contractor shall provide training to two separate groups of users, namely System Maintainers (generally the PAS contractor) and System Operators (generally the facility occupant). In general, the training shall include presentations, informal discussions, demonstrations and hands-on practical demonstrations on the systems installed. Training must include use of the Facility User Guides - FUGs (or final drafts) where FUGs are specified as a project deliverable. Training for System Operators shall cover all the functions and activities that the operators need to carry out on a daily basis. The training for the System Maintainers shall include that provided for the System Operators and additional training necessary for the system’s ongoing maintenance and administration. Further, the System Maintainer training shall also include training on how to instruct other staff by way of a ‘Train the Trainers’ approach. Facility maintainer and user representatives must be engaged in the development of training material and/or prior to the conduct of training to ensure the scope of training covers all requirements. Timing of the training must be agreed between the contractor and the maintainers & users, but must be completed prior to handover of the facilities and systems to Defence. The contractor must make provision for training of users and/or maintainers on multiple work shifts. Generally this type of training would be for more complex and bespoke equipment. Train-the-trainer. Where train-the-trainer requirements apply, training and training material must enable Defence staff and/or contractors to provide ongoing instruction for system maintainer and system operator training. A minimum number of train-the-trainer trained staff must be agreed with the maintainer and operator representatives. Maintainer and user representatives must be engaged in the development of training material and/or prior to the conduct of training to ensure the scope of training covers all requirements. | Training provided for the operator and maintainer and/or train-the-trainer a. a copy of the training syllabus; b. a list of attendees and the competency levels achieved; and c. PAS email confirmation is provided stating the training is completed in accordance with the requirements agreed to satisfy HOTO criteria 3.0
HOTO
5 | Design & Build Compliance Construction completed to approved design and all variations to original design IAW the BWM requirements. | The Contractor shall ensure that all design and installation is compliant with legislated requirements (federal, state) and Defence policies where applicable. Includes all “vertical” and “horizontal” assets e.g. Civil / Structural Engineering Services, roads, paths and car parking etc. All design and build variations and/or deviation from the certified design must be approved in accordance with the requirements of NCC and the BWM. The contractor is to obtain the Certificate of Completion for the building works in accordance with the requirements of the MFPE, NCC & Building Works Manual (BWM). A Certificate of Completion is provided by a qualified and experienced building surveyor when all the requirements nominated in the Building Works Manual are met. Note 1: A Certificate of Completion is a certificate issued by a building surveyor indicating that a building is substantially complete and occupancy of the building associated with the building approval is permissible. Note 2: If the works to be completed in a project are for multiple buildings within a complex, the contractor and PMCA / PM are to ensure that all stakeholders are aware including the occupant(s), that there will be a staged or phased handover and the buildings / infrastructure will not be completed at the same time. Each building will be handed over at the end of the project or agreed project stage once all checks are completed and the building is determined safe and fit for purpose. Performance Solutions. Where a departure from the "Deem to Satisfy" (DTS) provisions of the NCC is proposed or there are no applicable DTS provisions , a performance solution is required to demonstrate compliance with the relevant performance requirements. Dispensations. Any non-conformance with the Defence policy requirements must be addressed via a dispensation. Note. Where performance solutions and dispensations are proposed in the same building, a combined ‘Request for performance solution and dispensation’ form may be used where permitted by the policy owner. Note 4. The PMCA/PM shall ensure all Project to Policy Owner(s) interactions are recorded in the Project’s EGIS Project Report (EPR). | Certificate of Completion for each building and a copy of the staged occupancy plan. Copy of approved dispensation submission / form. If applicable. Copy of approved performance solution submission / form. If applicable. |  | OBJECTIVE: Building Works Manual | DPN: Building Works
The contractor must ensure that all works (including exempt building works as defined by BWM) comply with the WHS Act. Division 3 of the WHS Act ‘Further duties of a person conducting a business or undertaking’,. Specific duties include: a. Section 23. Duties of a person conducting business or undertaking that manufactures plant, substances or structures. The manufacturer must ensure, so far as is reasonably practicable, that the plant, substance or structure is manufactured to be without risks to the health and safety of persons. b. Section 25. Duties of a person conducting business or undertaking that supply plant, substances or structures. The supplier must ensure, so far as is reasonably practicable, that the plant, substance or structure is without risks to the health and safety of persons. c. Section 26. Duties of a person conducting a business or undertaking that installs, constructs or commissions plant or structures. The person must ensure, so far as is reasonably practicable, that the way in which the plant or structure is installed, constructed or commissioned ensures that the plant or structure is without risks to the health and safety of persons.
5.1 | Defect Liability Period (DLP). DLP management procedure provided, defects list & rectification schedule provided by the contractor representative including any register of outstanding defects, non-delivered project outcomes and rectification plan. | DLP Management Procedure. In consultation with the PAS PSS and PMCA / PM, the contractor is to develop and submit a DLP procedure which clarifies the avenue for defect rectification or to gain warranty maintenance. This procedure must include, as a minimum: a. Management procedure including: (1) detail clearly stating if the Contractor is the focal point for DLP and responsible for all defects within the period or will the PMCA / PM / PAS act as a liaison between Defence and the Contractor; (2) clearly differentiate between areas / locations of refurbished facilities that have an PAS maintenance responsibility for the DLP; and (3) a flow chart showing the steps to be taken to ensure the correct authority is contacted for the individual defect / requirement. b. Points of contact for: (1) types of defects; (2) scheduled, performance and responsive maintenance; and (3) after-hours emergency maintenance. c. Timelines for rectification to be completed for routine and urgent defects. d. Appropriate authority for validation / authorisation and acceptance of works completed under DLP. e. A finalised servicing schedule to be completed by the responsible person during the DLP and what that servicing actually included. HOTO Caveat Logs. Where applicable Caveats, issues and deliverables not provided are to be documented in the HOTO Caveat Logs. | DLP management procedure. This may be in a flow chart. Email from PAS acknowledging acceptance of procedure. Copy of Defects list and rectification schedule. Provision of agreed HOTO Caveat Log. (Refer to Tab 5)
Defect list & Rectification Schedule. The contractor is to provide a rectification plan and list of outstanding defects to be rectified and/or non-delivered project outcomes or works post the date nominated on the completion certificate. Caution must be taken to ensure that a defects list and that the non-delivered project outcomes list have a delivery / completion schedules that are monitored and completed satisfactorily prior to the conclusion of the DLP. A copy of the defects list must be provided to attendees conducting HOTO inspections and meetings. This defects list and rectification plan must detail as a minimum: a. a detailed description of the defects, b. description of criteria and evidence (aligned with HOTO) to confirm compliance rectification, c. person responsible for rectification, d. a date for the items to be rectified, and e. details and schedule for required DLP rectification review meetings specified at criteria 6.1
5.2 | Unexploded Ordnance (UXO) certifications with maps and GPS points of boundaries clearance (plus to the required depth) | There are many areas on the Defence estate confirmed as, or suspected of being, affected by UXO as a result of military activities, historical military exercises and ammunition burials. The Directorate of Contamination Assessment Remediation and Management (DCARM) through the National Unexploded Ordnance Program (NUXOP) has produced UXO Hazard Reports, including maps, for the major Defence Training Areas (TA). The purpose of the reports is to allow the inclusion of UXO as a factor when conducting risk assessment for any given activity on the TA. Mitigation of the UXO risk remains the responsibility of the individual who is authorising these activities. Should you require further information about the UXO Hazard Reports/Maps or have information that you think may alter the hazard levels shown on the maps, contact the NUXOP via the UXO inbox at: nuxo.program@defence.gov.au Basic Safety Practices. If you come across UXO on the Defence Estate you should: • NOT touch, disturb or tamper with the item in any way. This includes making any attempt to move the item to a ‘safe’ location. • Record the item’s appearance and location. • If possible, mark the location so that it can be easily found later. • Report the item to Range Control via your supervisor. Further information. Defence Intranet - Unexploded Ordnance (UXO) On Defence Estate Public Website - https://uxo.defence.gov.au/ | Where applicable, an email confirming that all UXO certificates and data have been submitted to nuxo.program@defence.gov.au and uxo@defence.gov.au |  | uxo@defence.gov.au | DPN: Unexploed Ordnance (UXO) On Defence Estate | DPN: Defence Unexploded Ordnance Management Policy | DEFENCE.GOV: National Unexploded Ordnance Program | DPN: Defence Unexploded Ordnance Management Manual
5.3 | Services Surveys and Testing Reports | Development of reports or surveys is undertaken during all stages of the project. The investigations should be programmed by the contractor and reports recorded and filed in the Objective project folder as they are produced. Do not wait until the end of the project to undertake the recording and filing activities. These may include but are not limited to: third party audits, investigations, services location searches, Estate Information extracts via Ground Penetrating Radar (GPR), tests undertaken and results provided (Geotech Surveys, Field compaction, including tests for Fuel Services Branch), As Built Data; and reports for hazardous areas, WHS, lighting and dilapidation etc. Reports and survey information are produced at different intervals during the project lifecycle and they should be saved to the approved Defence information repository (objective) by the PMCA / PM, PAS PSS and/or EMP (as agreed & applicable) once approved copies are released for use. Acoustics Test Results Technical Security Counter Measures (TSCM) Certification (DSVS where required) All projects (as required) shall have a Commissioning and Handover Plan that includes applicable acoustic testing for the commissioning of equipment and systems. Acoustic testing is required for certain conference rooms and higher classified areas. This requires an acoustic engineer to design, test and certify that will inform and support DS&VS or ASIO Technical Security Countermeasures (TSCM) Certification. | A list of all services surveys and testing reports provided, where applicable. Email notification from PMCA / PM, PAS PSS and/or EMP (where applicable) that listed reports where received for saving on Objective.
5.4 | Handover key schedule completed and attached with full set of tagged keys provided | The majority of new construction projects will require handover of keys at the end of the project. There will, however, be occasions where progressive handover of keys to Defence will be necessary. Initial handover of keys is to occur with and be secured by the Base Services team representative until HOTO is completed. Base Services team representative will provide keys to the RU when HOTO is approved and RU occupancy ready. In either case the contractor representative is to ensure a consolidated list of keys (including number of copies) is developed, a schedule for handover of keys is provided and all keys are tagged to identify what locks they are keyed to operate. The contractor and PMCA / PM are to ensure all keys (including copies) are accounted for and have transfer document signed to confirm handover. Keys for SCEC Hardware. The handover of key and key / hardware list for SCEC hardware is to be arranged between the SCEC hardware supplier / installer and the Base Security Officer and/or specified applicable tenant (Unit) Security Officer. Cylinders used within the locks during the construction phase are not to be the final SCEC cylinders. Keys for ICT cabinets and pits are provided to Telstra Infrastructure POC. | At HOTO consolidated list of keys and a signed transfer sheet; and where SCEC hardware is applicable, written notification from the specified applicable Security Officer that keys and key / hardware list have been received.
5.5 | High Risk Plant or Equipment essential operating instructions and/or diagrams and relevant logbooks are in place and certification certificates provided | High risk plant includes but is not limited to those items of plant specified in relevant legislation as being high risk plant and is not to be confused with Registrable Plant which is covered elsewhere in the HOTO. Whilst not registrable plant by definition it will almost definitely be plant requiring registration of design. In most cases high risk plant will include plant involved in work or activities defined as being high risk work. Such plant will require, as specified above, certain documents to be present and maintained to ensure Defence as the PCBU are compliant with relevant duty of care provisions. High risk plant will also include those items of plant requiring specific licences or accreditation to operate or own (e.g.. RADHAZ equipment, boom type EWP, scaffolding etc.). During construction the contractor is to identify where legislated requirements mandate log books and/or wiring diagrams are to be fitted. Essential operating instructions and diagrams shall be provided adjacent to plant and equipment controls. These instructions can include but are not limited to: a. O&MM often provide instructions (examples of signs) for the use of equipment / systems that are desirable to be signposted. b. Operating parameters to warn operators of incorrect operation such as: temperature and pressure ranges showing normal operating temperatures and pressures. c. Signs providing location of other equipment / valves etc. which need to be operated in conjunction with the equipment being operated. d. Signs, labels and other notifications must be manufactured from materials suitable for the area of fitting and exposure and shall be designed to ensure long life and indelibility. Laminated paper copies are not acceptable. All high risk and licenced P&E which is provided as part of the delivered works must have the manufacturer’s documentation providing the technical data and/or standards of compliance for the individual items. The project is to provide certification for all P&E installed. Examples of this include: Hazardous facilities, pumps, filters, air conditioners, refrigerators, electrical switches and components etc. These certificates are to be saved in Objective EM folders for applicable building and/or base infrastructure systems. | Email from PMCA / PM that Defence requirements for essential operating instructions and/or diagrams have been met. A list of logbooks and wiring diagrams and email from PAS stating satisfaction with their provision / placement.
5.6 | Registerable Plant essential operating instructions and/or diagrams, logbooks, test certificates are in place including design registration. | Legislation and/or Defence Policy mandates that certain types of plant i.e. boilers, cranes and pressure vessels must be maintained to comply with specific standards. The Defence Technical Instruction for Management of Registerable Plant (RP) is mandated for use by the BSC for estate upkeep. Regulation of registrable plant is monitored by Comcare. Defence uses GEMS to record and maintain RP data and conducts audits of that plant and records which is reported to Comcare. The Technical Manual mandates the documentation necessary to comply with the RP Comcare requirement including a current inspection and test certificate located at the RP confirming to all users the equipment’s registration is current. In addition, the project is to provide all data for the RP on the GDL and a copy of the manufacturers Design Registration Certificate is to be provided to Defence and filed in the Objective equipment item folder within the Estate Maintenance folder hierarchy. The contractor is required to develop a procedure for the Design registration of plant items to assist Defence in meeting its obligations under the WHS Regulations 2011. The Regulations 2011, specifically Division 3 – Registration process for plant designs, and the Code of Practice “Managing the Risk of Plant in the Workplace” must be consulted in detail to develop an appropriate procedure. Additional information about Defence registerable plant requirements can be found via the Defence Intranet link provided : | A list of: Registerable Plant operating instructions, diagrams and / or logbooks, test certificates displayed at equipment and the location for each item listed. Copy of Design Registration Certificates. Email from PAS PSS stating satisfaction with their provision / placement |  | OBJECTIVE: Management of Registerable Plant in SEG | DPN: Mechanical Engineering
5.7 | Radiation safety considerations i.e. Radiation Apparatuses (removal or addition) | In some cases there will a need to consider Radiation safety. The Contractor needs to consider the following: 1. Requirement to inform SEG Directorate Work Health & Safety (DWHS) when radiation apparatuses are sourced (for example: x-ray machines, baggage and mail scanners, bird scaring lasers, security scanners, soil density scanners). 2. When MILIS items (military integrated logistic information system) such as lasers used in shooting ranges, lasers used on rocket launchers, compasses with tritium are acquired, they must be registered with Defence Radiation Safety and Assurance (DRSA). 3. Requirement to inform DWHS when radiation apparatuses are disposed of during the renovation works. Before we can officially dispose of radiation sources, Defence is required to obtain prior approval from the Radiation Safety Agency CEO. 4. Requirement to inform DWHS if existing radiation apparatus’ are been moved, changed or modified during the HOTO process. The Security and Estate Group Radiation Safety Management Program (SEG RSMP) details how radiation is managed within SEG. The program aims to provide necessary information for managing all instances of using radioactive materials, for example X-Ray Baggage Machines, by SEG workers. It also provides guidance on our responsibilities in managing radioactive materials on behalf of Defence. SEG Directorate of WHS provides administrative assistance with completing these forms and is the first point of contact for dealings with radiation including acquisition, disposals, and movement etc. Defence Radiation Safety and Assurance are the only point of contact for Defence to the government radiation regulator, ARPANSA. Groups, Services and/or Projects must inform DRSA: *of any inventory changes *of lost or missing controlled radiation sources *prior to disposing of a controlled radiation source - please complete webform AE168 and email to SEG.safety@defence.gov.au.. *prior to purchasing or introducing a new controlled radiation source - please complete webform AD824 and email to SEG.safety@defence.gov.au *during the procurement phase for new equipment to determine if the item is a potential radiation source | Where applicable provide: A copy of any DRSA notification. Completed AE168, Completed AD824, |  | DRN: Internal Regulation and Assurance | OBJECTIVE: Radiation Safety Management Program | OBJECTIVE: Defence Radiation Safety Manual (DRSM) | EMAIL: SEG DWHS
5.8 | Emergency Evacuation Plans provided electronically and physically attached to the facilities. | Where a new facility has been constructed or an existing facility has been refurbished or changed to an extent that the floor plan / building layout is reconfigured and / or emergency exits have been moved and that is not accurately represented on the buildings current emergency evacuation plan, the project is to develop, manufacture and install / replace a block evacuation plan. The contractor is to comply with the following as a minimum for development of emergency evacuation plans: a. finding (or developing) appropriate floor plans; b. draft an Emergency Evacuation diagram based upon AS3745; and c. seek input from resident unit. The contractor is to produce or reproduce the fire evacuation diagram in the compliant format and quantity and install in the building in accordance with AS3745. | Certificate of Completion. Provide a list of where Emergency Evacuation Plans have been updates and/or supplied new – where applicable. Provide an electronic copy of plans.
5.9 | Notifying critical equipment and / or critical spares | Projects that deliver new critical assets or change / refurbish existing critical assets must provide a list of those assets to the PAS. PAS are responsible for creating / updating Critical System Recovery Plans (CSRP). Critical systems are those depicted in the estate data (ERIM or GEMS) where the Criticality attribute (1075) = Y. The criticality is determined on the ERIM Estate Class (EC) of the asset combined with the Contribution Factor (CF) attribute (1215) of the record = 1 or 2 (the importance to Defence capability). Note, an EC with a criticality of 'no' will always be no. EC's with criticality of 'yes' will only retain this rating if the CF of the particular item shown in the data is 1 or 2. By example, Residual Current Devices (Estate Class E.El.08.10) have Criticality = Y in the ERIM Estate Classes tab. Individual Residual Current Devices will have attribute 1075 Criticality = Y, only when attribute 1215 Contribution Factor = 1 or 2. The contractor is to also provide a list of critical spares supplied and/or recommended to ensure timely repair / maintenance of critical systems & equipment. Critical spares may be classed by their lead time for supply, local supply availability, cost, criticality to enable system operation. | PAS PSS to provide an email acknowledging receipt of an applicable critical asset & spares list.
5.1 | All Fire Safety Systems, Equipment, Monitoring, Alarm and Suppression System Installations meet applicable AS, MFPE and NCC requirements. | Where fire systems and equipment have been installed during a project to the level of protection required, baseline documentation is to be provided. Documents required to comply with fire requirements are detailed in the MFPE and BWM. This includes the Certificate of Completion and associated supporting evidence as required by MFPE. Where alarm and/or monitoring equipment and components connect to an existing system, PAS must be consulted for design, commissioning & testing. This evidence - where applicable - includes: a. Building Criticality Assessment Form; b. Hangar Assessment Form; c. Approved Dispensations; d. Approved Performance solutions; e. Fire safety management strategies; f. Frequency of Fire Safety Surveys IAW Chapter 6 of MFPE g. Evidence of consultation with the responding fire services; h. Services design documentation and design certificates as appropriate; and i. Specialist practitioners design certificates as appropriate – e.g. bushfire, access, etc. Fire systems, equipment and Defence associated requirements include, but are not limited to the following: a. Fire Hydraulic System Installations (fire hydrant and hose reel systems) approved & licensed Contractor certification; b. Emergency & Exit Directional Lighting systems. c. Smoke Detection & Occupancy Warning Systems,. d. Mechanical Ventilation and Exhaust Systems. e. Fire Suppression and Flooding Systems. f. Certification of Installed Handrails, Stair and Balustrade Systems. g. Evidence of fire vehicle access IAW Chapter 2 of MFPE. h. Extinguisher & Fire Blankets installed IAW MFPE and NCC. i. Passive Fire Protection (PFP) installation including the use of fire-resistant walls, floors, and doors. j. All Fire penetrations to be identified and registered as per AS1851. Where the above systems, equipment and/or requirements are applicable to a project, suitable evidence must be provided for each. | Applicable ITPs and ITRs. Installation Certificates. Email from PAS PSS confirm successful operation when integrating into existing systems.
5.11 | Electrical Test Certificates | Electrical test certificates and statutory authority certificates or independent certifier for electrical systems and equipment. (include: earthing systems, switch boards & gear, distribution pillars works tests). The contractor shall ensure all designs and installations are compliant with legislated requirements (federal, state and local), Manual of Infrastructure Engineering - Electrical (MIEE), and Defence policies where applicable. Where certain circumstances apply e.g. hazardous areas, an independent certifier is used to provide an additional layer of compliance validation. Earthing systems include equipment and structures for aircraft earthing points, HV earthing grids and general building earthing. ITPs provided as evidence of compliance must show resistance test results that meet the required Australian Standards and Defence instructions. It is essential that an appropriately qualified electrician, with hazardous area qualifications, be used within hazardous areas. All electricians working within hazardous areas are either to provide evidence of their competencies or applicable licenced details. Compliance and conformance requirements are satisfied and demonstrated by meeting the criteria specified in the BWM. In addition to the achievement of HOTO criteria 5.0 and issuance of a certificate of completion, contractors are to provide ITPs & ITRs and Installation certificate (BWM chapter 3) for electrical services if applicable.MIEE Compliance may include provision of, or update to:- Main Switchboard, Distribution pillar and board labelling, single line diagram schematics (installed or as amended), network diagrams, protection, load flow and earthing studies and arc flash reports as required. | Certification / statement of compliance: a. Installation certificate; b. Evidence of electrical load balancing over all 3 phases; c. ITPs & ITRs and electrical safety certificates, d. Switching authority certification with Hazardous areas (when applicable)
5.12 | Hazardous Area and Explosives Area Verification Dossier | The contractor shall ensure all designs and installations are compliant with legislated requirements (federal, state), and Defence policies where applicable. For Hazardous Area and Explosives Area equipment and systems the MIEE is to be used and in particular Chapter 15 and DEOPS 101 where applicable. | An compliant Hazardous Area and Explosives Area Verification Dossier |  | OBJECTIVE: Manual Of Infrastructure Engineering - Electrical (MIEE) | DRN: Explosive Ordnance Branch
5.13 | Mechanical test & commissioning results | The contractor shall ensure all designs and installations are compliant with legislated requirements (federal, state) and Defence policies where applicable. Compliance and conformance requirements are satisfied and demonstrated by meeting the criteria specified in the BWM. In addition to the achievement of HOTO criteria 5.0 and issuance of a certificate of completion, contractors are to provide ITPs & ITRs and Installation certificate (BWM chapter 3) for mechanical services if applicable. | ITPs and ITRs. Installation Certificates.
5.14 | Hydraulic test & commissioning results | The contractor shall ensure all designs and installations are compliant with legislated requirements (federal, state) and Defence policies where applicable. Compliance and conformance requirements are satisfied and demonstrated by meeting the criteria specified in the BWM. In addition to the achievement of HOTO criteria 5.0 and issuance of a certificate of completion, contractors are to provide ITPs & ITRs and Installation certificate (BWM chapter 3) for hydraulic services if applicable. | ITPs and ITRs. Installation Certificates.
5.15 | Security inspections have been completed and passed | All (relevant) projects will require a level of security to be allocated to the estate. To ascertain what this entails the contractor may to contact DS&VS, ADF ESA or tenant Security Officer or Security Manager for guidance. See appropriate process to link and the Defence Security Policy Framework (DSPF) and MFPE provides additional guidance. To engage and/or receive SME advice from appropriate DS&VS points of contact, contractors should call 1800 DEFENCE. Further information can also be obtained from the DS&VS portal. | Certificate of compliance with the appropriate security requirements, and inspection report from Defence Security Unit (where applicable). |  | Protective Security Policy Framework
5.16 | Physical Security Certification | It is the contractor's responsibility to comply with the DSPF and engage with the following individual DSV&S and/or ADF Facility Security Certification Authorities to ascertain if an inspection is warranted to achieve approval for the final constructed or installed security level: a. ARMY from 15 Jul 2021 to 01 Feb 2022 Physical Security Certification and Coordination Cell (PSCCC) usual operations will cease, therefore an Interim Authority To Operate (Minute - BQ25515978) has been issued requiring affected units to conduct a Security Risk Assessment (SRA) to manage non-compliance with accreditation during the pause. (temporarily suspended - Army. DPU requests are submitted via an AE624. AE624 Instructions provide assistance to complete the request.) b. RAAF. RAAF Security Force (SECFOR) provide a security and policing capability to Air Force that supports force protection and the maintenance of morale and discipline. c. Navy. Deputy Director Navy Security provide a security and policing capability to Navy that supports force protection. d. DS&VS. For larger projects DS&VS will be the certification authority with input from SCEC Security Zone consultants. Sponsor and/or user organisations can advise the operational requirements which will help inform the determination of instruction & certification requirement. | Final inspection report from the certified security agency or an email advising a final inspection is not required. A report must include photographic evidence and close up inspections where required e.g. ceiling spaces and voids, approved variations are documented and SCEC consultant sign off that the construction meets the security design.
5.17 | Commissioning for security systems, alarms, and access control systems including training | The contractor shall ensure all designs and installations are compliant with legislated requirements (federal and state), and Defence policies where applicable. Where alarm and/or monitoring equipment and components connect to an existing system, PAS must be consulted for design, commissioning & testing. | Facility Certification from DS&VS, ADF ESA or ASIO-T4 (for Security Zone 5). Installer commissioning documentation and SCEC consultant sign off for Type1A alarm systems. Email from PAS PSS to confirm successful operation when integrating into existing systems.
5.18 | O&MM for security systems, alarms and access control systems provided to Unit Security Officer | At the completion of the project the contractor is responsible to ensure all security information and hardware is provided to Defence. This will include but is not limited to O&MM, Keys and Codes and/or combinations. Keys for SCEC Hardware. The handover of a key and key / hardware list for SCEC hardware is to be arranged between the SCEC hardware supplier / installer and the Base Security Officer and/or specified applicable Facility Security Officer. O&MMs. Generally operations and maintenance requirements for equipment systems are documented in the building and/or base infrastructure O&MMs. However where the security classification for the security system and O&MM details are classified higher than "Official", a dedicated security O&MM is to be created and supplied to the applicable Base and/or facility security office for storage on an appropriately classified information system. Alternatively a hard copy can be produced and stored with the equipment in the applicable equipment cabinet, where the security classification of storage requirements are appropriate. | Email from Facility Security Officer acknowledging and accepting receipt of applicable items. i.e. O&MM, keys and access codes and/or combinations.
5.19 | Certification / Accreditation for Sensitive Compartmented Information Facilities (SCIF), Magazines and Armouries and Zones 2 to 5. | At the completion of the project the contractor is responsible to ensure all security information and hardware is provided to Defence. This includes certification and accreditation of sensitive estate such as magazines, armouries and security Zones 2 to 5. The contractor is responsible to approach the appropriate certification group during design and/or commencement of construction to ensure all requirements are provided during construction. | Certification / statement of compliance from the installation contractor stating what the installation complies with SCIF construction plan and armoury construction guidelines. Copy of the assessment certificate / notice from the inspection & accreditation agency advising the facilities comply with Defence required policy and standards. . |  | DPN: Defence Security Principles Framework
5.2 | Updated Defence Engineering Service Network (DESN) configuration and management documentation impacted by project works | Where delivered works add to or alter existing systems which have an existing DESN for the establishment (or maybe linked to outside areas e.g. Fire), delivered works are to be connected to the existing DESN. For example, additional smoke sensors are to be connected into the existing building FIP and/or connected to remote monitoring sites. Where equipment and components connect to an existing system, PAS must be consulted for design, commissioning & testing. Examples of DESN include fire activation and/or monitoring, emergency lighting, building management systems, SCADA and power metering. These are non JCG managed networks and passive infrastructure, however JCG may be contacted to provide SME advice from time to time. | ITR for commissioning. Email from PAS PSS verifying successful operation when integrating into existing systems.
5.21 | Voice and Video Phones system commissioned and connected to existing base infrastructure | The contractor shall ensure all designs and installations are compliant with legislated requirements (federal, state and local), and Defence policies where applicable. Where a Voice or Video Phone system has been affected as part of delivered works the project is to ensure all passive infrastructure (e.g. caballing etc.) is installed and tested to the standards required by JCG for the purpose of completing HOTO. Installation and commissioning of the active equipment (phone handsets, PABX etc.) will be installed and commissioned by JCG approved contractors in the DLP period. | Commissioning ITPs and ITRs, Email from JCG or Telstra verifying successful operation and/or integrating into existing systems (where applicable).
5.22 | Defence Data Networks (Passive infrastructure works) are commissioned and connected to existing base infrastructure. | The contractor shall ensure all designs and installations are compliant with legislated requirements (federal, state) and Defence policies where applicable. Where Defence data network (passive infrastructure) works have been conducted as part of delivered works the project is to ensure all systems are commissioned to the standards required by JCG. Whilst passive infrastructure is installed and commissioned by the contractor, JCG are required to receive commissioning test results and updated and/or new network drawings etc. and JCG can be engaged to assist in validation of those results. Requests for JCG assistance can be logged via the JCG web site. (Passive ICT Compliance achieved part of project via JCG Telstra ROS). | A list of all security items and/or network drawings handed to ICT which has been signed as correct by JCG and/or Telstra where applicable.
5.23 | Keys for communications rooms, cabinets and infrastructure pits have been installed to Defence Security Principles Framework (DSPF) and Information Security Manual (ISM) standards and handed over to Regional ICT | Where new communication infrastructure has been delivered there is a requirement to ensure appropriate security is applied to protect unauthorised access and/or tampering. Defence security standards are outlined in the Defence Security Principles Framework (DSPF) and/or the Information Security Manual (ISM). All physical security items (keys etc.) must be provided to the regional ICT representative with an appropriate transmittal form detailing all keys (correctly tagged for identification), number of copies and location of items and any security documents detailing the originator of the locks etc. Requests for JCG assistance can be logged via the JCG web site: 'JCG Log A Job' | A list of all security items handed to ICT which has been signed as correct by JCG and/or Telstra where applicable. Copy of signed receipt from JCG / Telstra |  | DRN: ICT Service Center
5.24 | ICT systems commissioned and accepted by JCG | Varied types of ICT systems (including active equipment ) can be associated with the project scope and deliverables. Typically, the different ICT system types are categorised as Base Management Systems (BMS), capability manager owned systems or JCG Corporate Systems. For BMS, the Contractor is to commission and test all installed passive and active equipment, infrastructure and systems. For JCG corporate systems Passive assets & infrastructure (i.e. cabling etc.). These are typically installed by the works contractor. These assets must be tested by the works contractor and test results are to be provided to JCG. Active assets & infrastructure (i.e. PCs, servers, switch equipment etc.). These are installed by JCG and their approved contractors. The installation, commissioning and testing of active assets is done during the DLP phase and is not the responsibility of the contractor(HC). Therefore, completing the installation and commissioning of active assets for JCG corporate systems is not required to effect HOTO completion. Capability Manager owned systems Installation and testing of passive assets and infrastructure may be done by the Contractor, however all active assets and infrastructure is a capability Manager responsibility. The PMCA / PM must ensure that JCG are notified early in the delivery phase if JCG Corporate Systems are required to conduct defence business. A copy of the JCG corporate system passive assets, commissioning ITP and ITR are to be provided to JCG / Telstra ROS. | Commissioning ITPs and ITRs, JCGG Corp System. Email from JCG or Telstra verifying successful operation and/or integration into existing systems (where applicable). BMS. Email from PAS verifying successful operation and/or integration into existing systems Capability Systems. Email for Capability Manager verifying successful operation and/or integration into existing systems.
5.25 | List of all hazardous chemicals - quantity / type and storage system of fuels, chemicals or lubricants for uploading into ChemAlert. | Hazardous Chemicals policy and procedures are contained in the Defence Safety Manual Volume 3, Part 3A, Chapter 1, [with the prefix HC]. These form the basis for a consistent, comprehensive and inclusive, 'whole of Defence' system for the management of Hazardous Chemicals. The WHS Manual mandates all RU hold details on all hazardous materials used by its staff or held within its area of responsibility. To achieve this all new works are to provide a complete list of hazardous materials delivered under the project so as to be incorporated into appropriate registers and/or manifests. | A complete list of hazardous materials to Base management team, resident unit and/or PAS where applicable. Email copy of receipt from Base RU and / or PAS.
5.26 | ECC Post Activity Report (PAR) Signed. | The PAR detailing any / all environmental incidents that occurred during or as a result of a project. The PAR is to fully detail the event(s), issues arising from the event(s), all rectification actions, effectiveness of the rectification issues and outstanding issues. Not all Environmental Clearance Certificates will need a PAR. The Zone ESO will note within the ECC if a PAR is required or the Contractor will be advised during the project in the case of an unforeseen event during the project. When in doubt the Contractor is to contact the Zone ESO to determine if a PAR is required. | A copy of signed PAR.
5.27 | Reporting Environmental Incidents | All environmental incidents are to be recorded on the PAR sent to Zone ESO. Incidents are also to be reported and actioned via the GEMS Incident Report Form. Refer to the Environmental Incident Reporting Guideline located on defence.gov.au. An exception applies to Navy environmental incidents including whale strikes, foreign fishing, sewage spills, fuel spills and other marine pollution, specified greenhouse gas emissions and marine pest fouling. These must be reported through the Navy Safety Environment Reporting System (SERS) http://sers.dpe.protected.mil.au/sers/ The Environmental Incident Procedure provides detailed instructions and information to report incidents. The Contractor is responsible to ensure the ECC and PAR are reviewed and signed by the Zone ESO. | Copy of GEMS incident Report Form - or GEMS ref # |  | DPN: Environm​ent and Heritage | DEFENCE.GOV: Environmental Incident Reporting and Management | EXTERNAL PDF: Environmental Incident Reporting and Management Guideline | EXTERNAL PDF: GEMS environmental incident reporting guide | DEFENCE.GOV Environment and Heritage Manual
5.28 | Provision of Contaminated Sites Management Plan. | The contractor is responsible for provision of a contaminated sites management plan for ongoing maintenance of residual contaminated site and materials. The Contamination Management Manual details the process for creating and submitting GDLs to update the CSR in GEMS. Note: The management of contamination, or contaminated materials / substances through project delivery is managed via the ECC process. | Evidence to include copy of correspondence to Base & PAS of agreed Contaminated Sites Management Plan and update of contamination site register. |  | DPN: Contamination | Objective: Defence Contamination Management Manual
5.29 | Provision of Environment Protection and Sustainability Management Plan. | All specific requirements for continued Environment Protection and Sustainability management have been identified and recorded in accordance with the inclusions of the relative PAS Land Management Description and Deliverables. This is inclusive of relative data, in accordance with NEPM natural assets and Environment Protection and Sustainability management estate classes to record required changes to the extant Plans, estate appraisal requirements and the supporting subordinate plans which may include but are not limited to Weed Management, Water Quality Monitoring, Overabundant Native Species, Threatened Species. Environment Protection and Sustainability means land management; waste management, animal management; water and energy requirements. | Evidence to include copy of correspondence to Base & PAS of agreed Environment Protection and Sustainability management plan. |  | DPN: Smart Infrastructure | OBJECTIVE: ​Defence Smart Infrastructure Handbook​ (Smarti)​ | DEFENCE.GOV: Landscape Management Manual
5.3 | Heritage management information provided for Heritage Management Plan | Defence environmental managers maintain a Heritage Management Plan which needs to be updated when works are conducted on heritage items listed within the plan. The Contractor is to provide details of proposed changes to heritage listed estate to the Zone ESO and inform the PAS PSS that this has occurred. | Copy of Heritage Management report provided to the Zone ESO. |  | DEFENCE.GOV: Environmental Incident Reporting and Management
5.31 | Smart Infrastructure requirements complete | Defence requires all new estate works design and construction projects to continuously improve the efficiency, effectiveness and sustainability of the Defence estate. Smart Infrastructure defines Defence requirements and reporting obligations for planning, design and construction covering energy, water, waste, pollution prevention, and smart procurement. The Smart Infrastructure Handbook: a. outlines Ecologically Sustainable Development (ESD) and Whole-of-Life (WOL) requirements for each project, covering: design, construction and associated reporting; and b. provides Smart Infrastructure Checklists that include a Metering Strategy. It is the Contractor's responsibility to ensure smart infrastructure principles are implemented into all design and construction of delivered works. The Government's Energy Efficiency in Government Operations (EEGO) policy requires Defence to develop and implement a comprehensive energy management strategy. This includes a metering, monitoring and management program to facilitate energy reporting against EEGO specific end use categories. Defence developed the NSP in response to the EEGO policy. To meet the Defence NSP objectives, the Resource Data Management System (RDMS) has been implemented. Electricity, gas and water meters installed under project works are to be connected to the RDMS and in accordance with the Handbook and hardware specifications under the heading ‘Meter Documentation’. Any new or replacement meters being connected to the RDMS need to have a relevant New Meter Form and Meter Hierarchy submitted to the RDMS Program Manager. | Provision of completed Smart Infrastructure Checklist (Smarti) |  | OBJECTIVE: ​Defence Smart Infrastructure Handbook​ (Smarti)​ | POLICY: Energy Efficiency in Government Operatios (EEGO) Policy | DPN: Smart Infrastructure | OBJECTIVE: Defence National Sub-meter Program Requirements
5.32 | Billing connection & dis-connection of energy; including solar, gas and water services. | Where project works include installation of a new connection, dis-connection or supply capacity increase / decrease for electrical, gas (natural and LPG), water and sewerage services involving the supply coming into a base, in addition to liaison and submission of applications for approval from external utility providers, a form AE879 is to be raised and sent to the Utilities Section of the Directorate of Specialist Contract Support (DSCS) at: des.contract@defence.gov.au (The AE879 is a purely internal document which provides information for the ongoing payment of accounts for the supply upon project completion.) DSCS should be contacted during the construction phase to assist contractors to understand the different responsibilities of network operators, retail service providers, Defence and the contractor. Modifications to internal reticulation may not require an AE879 and this can be discussed with DSCS. | Copy of submitted AE879.
5.33 | Software Provision of system software, software licences and all configuration files | Continued improvement of machinery and systems inevitably increases the use of electronic controls which in turn increases reliance on software to operate and/or maintain equipment. As a result Defence requires all software created for the project to be delivered with the project allowing for ongoing operation and maintenance. For installed equipment the contractor is to provide all software and configuration files including usernames and passwords. Where software is procured for the operation and/or maintenance of installed equipment, software licences are to be provided to Defence. | Software licence certificates, and email notice of receipt (EMP and/or PAS) for backed up copy of software and/or configuration files.
5.34 | Data Provision Checklist Actions & Deliverables have been completed and verified for HOTO Phase. | Where a Data Provision Checklist (DPC) is established and agreed at the commencement of the construction phase, DPC actions and deliverables are to be regularly reviewed and completed as early as practical. This criteria is met once the agreed once all DPC actions and deliverables (excluding DLP items) have been completed. Refer to the data provision checklist and data provision checklist Inst tabs in the HOTO Plan and checklist document for further information about DPC requirements. | HOTO Phase of the Data Provision Checklist completed.
5.35 | Asset Rollout pack Completed & Submitted for all new or refurbished facilities. | As per the Defence Project Accounting Manual (DPAM), when an asset or group of assets has been satisfactorily delivered by the contractor to Defence, it is to be rolled out from Assets Under Construction (AUC) to Assets in Use (AIU) by submitting a complete rollout pack. For CFI projects, the complete rollout pack is to be submitted to ID Finance for review. Once approved, ID Finance will forward the pack to the DFG Asset Accounting Team for processing. For all other projects, the complete rollout pack is to be submitted directly to the DFG Asset Accounting Team Fully completed rollout packs, with accompanying signed notification forms and NOCs are to be emailed to: For CFI projects: ID Finance group mailbox, ID Finance - MCF idfinance-mcf@resources.defence.gov.au For EWP & Other: AUC Correspondence auc.correspondence@defence.gov.au | A copy of the complete Asset Rollout email submission.
Project Takeover - Transition from PMCA / PM to SDD
5.36 | PAS PSS has attended site to confirm services for support in preparation for maintenance on Takeover | The local PAS PSS is to attend the final construction site walk through with the PMCA / PM, Contractor, stakeholders and the Defence Representative with the aim of: a. determining defects, estate information requirements and/or issues which must be completed prior to handover; b. ensure PAS have checked all delivered Plant and Equipment and confirmed support arrangements for agreed maintenance during DLP; c. providing feed back to the contractor on any additional information and/or training required; and d. identifying BSC service delivery areas which need immediate attention. | Minutes / Report for the final walk around activities that clearly document attendees and acceptance of outcomes / actions.
5.37 | Relevant support, services and maintenance for Base Services Contracts have been actioned and accepted by relevant service provider/s in preparation for DLP commencement. | The PAS is to confirm that all required relevant support services, operations and maintenance services (as provided by PAS , Miscellaneous Service Providers or Other maintenance agents i.e. Fuel Network Managing Contractor) are prepared and ready to enable facility occupation, use and sustainment, applicable for the commencement and end of DLP. In the Project Planning and Design phases PAS PSS must engage with the Project sponsor, RU, PMCA / PM, Zone and/or Product Directorate staff to understand and agree what BSC services and maintenance is to be provided for these periods. Ideally CCPs for the required services would be submitted & approved, however, at times this is difficult to achieve; so PAS must liaise with applicable Product Directorates to implement alternate arrangements to enable TO. i.e. survey and quote. | Email from PAS PSS confirming Service Provider/s acceptance of support, services and maintenance.
Defects Liability Period (DLP) & Project End |  |  | Achieved by evidence below.
6 | All Defence approved HOTO caveats and issues cleared | The PMCA / PM are to monitor and clear caveats, project issues and projects deliverables not provided, as recorded in the respective logs. Final payments should not be made until the contractor has fulfilled and delivered all contractual requirements of the project build and cleared recorded caveats and issues to the agreed standard. | PMCA / PM email confirming that all approved HOTO caveats and issues have been cleared, and required evidence is stored on the DEIS.
6.1 | NLT 28 days prior to DLP end date, all defects repaired and related estate data has been updated | The contractor is to ensure that all defects have been rectified and related estate data has been updated to the requirements specified in applicable HOTO criteria and evidence instructions and any other agreed requirements detailed in the DLP rectification plan and list. The PMCA / PM is to confirm all rectifications and evidence requirements have been met. At regular intervals during DLP (a minimum period of every three months and detailed in the defect rectification plan, criteria 5.1 refers) the PMCA / PM, PAS PSS, Zone EMP representative and contractor must meet to review progress to rectify defects according to the agreed defect rectification plan. PAS are to advise for PMCA / PM resolution, if they believe defects have not been satisfactorily rectified and cause an unacceptable residual impact or liability for the ongoing maintenance and support of the facilities. | End DLP checklist and Defects log completed, suitable evidence (as detail in the agreed defect rectification plan) is provided.
6.2 | 28 days prior to DLP end date, PAS advised and confirmed their readiness to commence agreed maintenance at the end of DLP (for CFI & by exception for EWP). | Depending on the project and the agreed maintenance plan, PAS maintenance may have commenced at the beginning of DLP, particularly for EWP projects. If the contractor and/or their subcontractors have provided maintenance during DLP, PMCA / PM is to ensure the contractor has provided the PAS, all logs and data for maintenance performed on facilities and equipment during DLP. When applicable, PAS PSS is to confirm that they have all necessary information (drawings, manuals and GEMS estate data) to commence maintenance and support activities. | A confirmation letter or email from PAS PSS.
6.3 | Data Provision Checklist Actions & Deliverables have been completed and verified for DLP. | It is expected that by HOTO, all Estate Data has been provided, validated for accuracy / completeness and GDL proved to PAS PSS. However there will be circumstances where items and/or defects will be identified during HOTO and DLP that require additional work or rectification. In these circumstances, the provision of remaining and/or corrected information to an agreed plan will occur. The contractor and PMCA / PM are to ensure and confirm to PAS PSS that all remaining and/or corrected estate data has been provided and saved in GEMS, drawings updated and/or O&MMs updated (where applicable) by the agreed delivery plan and before DLP end. PAS PSS is to confirm this has been achieved. | Completed copy of Data Provision Checklist for DLP Phase.
6.4 | Final Asset Rollout submission, including Works undertaken during DLP that add value to the asset/s. | At expiry of DLP for the final stage of the project, a final rollout is required for the remaining AUC balance. The remaining AUC balance can be sourced from ROMAN or the Project Manager/ Project Officer can: a. Determine the remaining AUC balance (sourced from ROMAN or the Project Officer); b. Determine value of DLP works undertaken; and c. Determine PMCA/PM, design and other fees for each stage/works package. PMCA/PM to complete the DLP Enhancement section of the Cost Allocation sheet and transpose values to the DLP Enhancement worksheet. Once the final rollout is complete the Project Officer can financially close the project. Completed DLP rollout packs, with accompanying signed notification forms and NOCs are to be emailed to: For CFI projects: ID Finance group mailbox, ID Finance - MCF idfinance-mcf@resources.defence.gov.au For EWP & Other: AUC Correspondence auc.correspondence@defence.gov.au | A copy of the Final Asset Rollout email submission.

## 7.Data Provision Checklist Inst
DATA PROVISION CHECKLIST INSTRUCTIONS
|  | Data Provision Checklist (DPC) Development | The Data Provision Checklist (DPC) - is to complement the contractor's Estate Information Provision Plan (EIPP). The DPC aims to provide contractors with sufficient information to plan and document a schedule for the submission project information & data throughout the project lifecycle and for the PMCA / PM and PAS PSS to validate receipt & completion in accordance with the contract conditions and HOTO requirements. When developing the EIPP and DPC, contractors must liaise with the PAS PSS to agree a schedule for data submission, checking and turn-around validation / processing times that enable related HOTO criteria to be achieved. Where DPC criteria / deliverables (rows) are not applicable or required for the project, "N/A" is to be selected in DPC column "D" - "Status Required".
| Project Phase | Data Provision Actions and Deliverables (DPC Criteria) | Description | Supporting Information | Comments | Links
| Design Phase | (
1 | Design | Data Extracts from GEMS provided to Designer (required for existing facilities, extending current infrastructure and/or upgrading existing assets) | Data extracts are to be taken to inform the design process and also identify what information will require updating as a result of the project. (Extracts should be used "for information only" purposes as GEMS data can be incomplete and/or inaccurate. Requests for these extracts are to be prepared using the Request Estate Data Form, to define the scale and extent of data to be included. The form can be obtained from the Estate Data Management "Forms" Objective link. If unsure of the extent of the current estate data, liaise with PAS PSS to ensure correct footprint is requested If after inspection of the GEMS data extracts it is found that data is missing or incorrect, and it inhibits the contractor from creating project related asset shell and data records via GDLs (e.g. where a functional parent is required but extracted data is missing or incorrect) the contractor is to create new shell and data records via GDL submission to address the problem. Where missing or incorrect data does not inhibit the project data creation requirements, PMCAs / PMs are to report the data anomalies to PAS PSS to initiate remedial action. Spaces Plan. Where a spaces plan is available for an existing facility, PAS is to provide a copy for project to reference and/or update as applicable. For a new facility the project is to create and provide a spaces plan for the facility. | Support \ Information Data Management Home page - EDGA Template and Forms - EDGA User Guidance - EDGA Business Rules - Help and Support Objective GDL Guidance Documents - Management Handbooks - Management, Rules and Instructions - GEMS Data Fields - Assurance and Validation Checklists - Templates and Forms Form Request Data Download Form |  | DPN: Estate Data Management Home Page |  | OBJECTIVE: GDL Guidance documents. | External access to Data Supplier/Contractor Toolkit resources ( this link will not open from within the DPN.)
2 | Design | The Project submits a GDL to PAS PSS requesting to create asset shell records for Buildings, Levels, Spaces, Infrastructure, Equipment Systems & Equipment (where known) etc. and provides a new or updated spaces plan. GDL and Spatial Data submissions are accompanied by relevant Assurance & Validation Checklists | Asset shell records are the minimum data attributes required to create an initial record in the GEMS database that can be added to later and are created using the GDL. GDLs are to be completed to request asset shell creation for all new assets using the endorsed Data Requirements documentation (Estate Class Mapping Diagrams for all Estate Classes, EBI Numbering Plan for Levels and Spaces). This is done early in the project lifecycle to ensure all dependant activities are founded on accurate shell records to reduce latter complications. Completed GDL requests are submitted to GEMS for processing. It may be beneficial for projects to request the creation of shell records for building assets earlier in the design phase once it is known how many new buildings may be required to ease the integration of EBIs into drawing Title block information. Note: creating new asset shells relates to shell records for Building, Level, Space, Infrastructure, Equipment and Equipment Systems where these are known in the design phase. | Support \ Information Estate Data Governance Application (EDGA) Home page Form EDGA GDL Template v1.3 GDL Assurance & Validation Checklist SDMP Assurance & Validation Checklist |  | OBJECTIVE: GDL Templates | OBJECTIVE: SDMP – Validation Checklist | OBJECTIVE: GDL – Validation Checklist | OBJECTIVE: Operation and Maintenance Manuals (O&MM) – Validation Checklist
3 | Design | PAS review GDLs and process in EDGA. Incorrect submissions are quickly referred back to supplier with detail about issues. | Add additional rows to record where GDL will be submitted / processed in more than one batch.
4 | Design | All required GDLs to create shell records have been submitted to PAS PSS by the 90% design - Building, Level, Space, Infrastructure, Equipment Systems & Equipment (where known) etc. | Confirmation from Defence that all asset shells have been created and generated within the GEMS and assigned EBIs returned to the project for integration into project documentation.
5 | Design | A list of compliant design drawings, minutes of design meetings and/or correspondence from stakeholders and SMEs identified in the agreed EIPP accepting designs. Design Drawings Completed - End of design phase. | Throughout the project design phase there will be several meetings and various activities conducted to ensure the required stakeholders are engaged, project scope and deliverables (including approved changes) are understood & agreed; risks and constraints are identified; and plans, designs and drawings are developed to the required standards. It is the designer’s responsibility to ensure that all design plans and drawings are complete (includes approved project scope and user requirements) and compliant with the contract conditions. To assist Contractors with development of estate information in the construction phase, final Design Drawings are expected to have title blocks that accurately reflect issued EBIs for Building\Infrastructure and floor\layout plans are to accurately reflect the issued space Identifiers.
6 | Design | Spaces Plan prepared IAW SDMP and submitted with completed SDMP Assurance & Validation Checklist. |  | Support \ Information Info Rule 005 - Building Space Records Spatial Data Management Plan Home Page - Primary resources: Section 4, Appendices H, Template & Example 4 Form SDMP Assurance & Validation Checklist |  | DEFENCE.GOV: Spatial Data Management Plan (SDMP) | OBJECTIVE: Info Rule 005 - Building Space Records | OBJECTIVE: SDMP Folder | OBJECTIVE: SDMP – Validation Checklist
Construction Phase
7 | Pre-mobilisation | Data Extracts from GEMS provided to Contractor Representative (required for existing facilities, extending current infrastructure and/or upgrading existing) | Data extracts are to be taken to inform the ongoing development, update and submission of GDLs throughout the construction phase. Requests for extracts is via use of the Request Estate Data Form obtained from the Defence Estate Information Page. If unsure of the extent of the current estate data, liaise with PAS to ensure correct footprint is requested. If the GEMS data extracts are missing data or the data provided is incorrect, after inspection, take measures to have these records corrected/updated/created. Contact the PAS, who will be able to guide the data supplier in the right direction to have this missing data created or incorrect data updated. | Form Request Data Download Form |  | OBJECTIVE: Request Data Download Form
8 | Construction | The Project submits GDLs with completedAssurance & Validation Checklist to PAS PSS requesting to Create asset shell records and / or Update asset records. Incorrect submissions are quickly referred back to supplier with detail about issue areas. | Large projects by nature are required to submit considerable amounts of data. The larger the project, the larger amount of information will be created. To avoid processing issues, reviewing and approving an entire project set of data can create unnecessary delays or other issues. Data submissions are to be broken down into logical batches where appropriate. For large and/or complex projects, incremental or a rolling provision of data could be expected from early in the construction phase to 90% construction or 28 day notice of completion. All GDL Submissions must be accompanied by an Assurance and Validation Checklist, a single Checklist may be used for multiple GDL's when submitted at the same time. If there have been any changes made to the design, check with the GEMS MDT to ensure that current shell records are consistent with the design change. If they are no longer accurate, create new shells records in a new GDL and advise PAS PSS & GEMS MDT of the changes/updates/deletions to be made. GDLs must take into account any updates (either New Asset or Disposal\Demolition) that have occurred over the period. These data submissions should also include any submissions or updates to hazards or asbestos data and any necessary environmental data using the appropriate EFR GDL. A GDL submission schedule is to be developed, agreed and circulated to representatives at the commencement of the Construction Phase and forms part of the EIPP. Where the provision and/or upload of GDLs is incomplete, the PMCA / PM, PAS PSS, the Zone EMP rep and contractor are to revise the EIPP and agree to a new data supply schedule as required. When submitting the initial Update GDL, the contractor is to ensure the DLP dates reflect the completion date programmed at the time of submission, noting that this date may change as the project nears completion. Should the completion date nominated in the initial Update GDL differ at the time of project completion, the contractor is to ensure that the final Update GDL captures these changes and the DLP dates are modified to reflect the accurate dates. If the final GDL has been accepted prior to the accurate DLP dates being known, and provided there are no other changes required, the contractor is to inform the PAS. In this situation the PAS will perform the update of the DLP dates. | Form EDGA GDL Template, GEMS EFM Interactive Form or other GDL Template, as advised by Defence SME or PAS Support \ Information Estate Data Management Handbook, step 13.4 .1 thru 13.5.3 http://www.defence.gov.au/estatemanagement/lifecycle/EstateDataInformation/Default.asp Defence Safety Manual Vol 3, Part 3A http://drnet.defence.gov.au/People/WHS/SafetyMan/Pages/SafetyMan.aspx |  | OBJECTIVE: GDL – Validation Checklist | DPN: Estate Data Management Home Page | OBJECTIVE: GDL Templates
9 | Construction | Additional GDL submissions, as required & determined by project. (all data for new or updated items is to be supplied via GDL by 90% construction). | Additional rows are added to the checklist to record the different batches and timing of GDL submissions to PAS. For large projects there may be many batches that align to project construction phase, as different facilities and/or assets are completed etc.
10 | Construction | PAS review GDLs and process in EDGA. Incorrect submissions are quickly referred back to supplier with detail about issues | With consideration of the contractor's proposed GDL submission schedule, PAS PSS are to determine and agree GDL processing times that are as minimal as practical (10 working days or less with consideration of data volumes and other PAS PSS workloads). Where errors are found, PAS PSS are to quickly advise the contractors and provide guidance about what items need to be rectified before GDLs are resubmitted by the contractor representative.
11 | Construction | RFI Notice to request Master Site Plan (MSP) for Update purposes issued to PAS PSS. | Master Site Plans (MSP) are controlled access documents and can only be issued to one party at a time for update and will only be issued for the minimum length of time to conduct the update. Projects are required to update this plan IAW the SDMP. Projects are to: a. familiarise themselves with the content\accuracy and submission requirements of the SDMP; b. submit a request to obtain a MSP once all major external works are completed; and c. collect by means of survey to satisfy accuracy provisions, all changes to the estate from the building line out. Updates to the MSP generally can occur once all major construction and landscaping works external to the building line are complete. Requesting this plan when this criteria is met may allow additional flexibility in the provision timeline in event the document is unavailable. Note: This can be initiated earlier in the process than construction, to allow for more efficient planning and management of the requirement/s, enabling validation by or before HOTO. | Policy Spatial Data Management Plan Section 3: Master Site Plan Datasets Section 6: Engineering Detail Survey Appendix G: Master Site Plan Dataset Standards http://www.defence.gov.au/estatemanagement/governance/Policy/SDMP/Default.asp |  | OBJECTIVE: Spatial Data Management Plan (SDMP) | DEFENCE.GOV: Spatial Data Management Plan (SDMP) | External GovTeams: SEG Records Management Contractor Guide | Objective: SEG Records Management Contractor Guide
28 Day notice of Completion (CFI project) or 90% construction for all other projects.
12 | Construction | Submission of all GDLs with accompanying GDL Assurance & Validation Checklist to PAS PSS - all data fields completed. | By this stage, all GDLs should have been completed (including necessary asset attributes) and submitted to the PAS PSS for review, validation and upload. |  |  | OBJECTIVE: GDL – Validation Checklist
13 | Construction | Submission of draft O&MM with accompanying O&MM Assurance & Validation Checklist for validation. | Draft O&MMs are provided to the PMCA / PM to confirm requirements specified in the contract and agreed EIPP delivery schedule have been met. Once these requirements are confirmed and the submission checked, the PMCA / PM is to forward the draft O&MMs to the PAS PSS for validation of completeness and meeting Defence O&MM Instructions. All O&MMs by this stage need to be prepared and submitted to review (either as draft digital media or notified draft completion for Online Document management system). O&MMs are to be checked and quality assured by the Contractor prior to submission to ensure all relevant content has been provided and completeness of all project relevant sections as required IAW the Defence O&MM Instructions. An Assurance & Validation Checklist is to be completed as part of this process. | Policy Operations and Maintenance Manual Specifications http://www.defence.gov.au/estatemanagement/lifecycle/estateupkeep/Docs/PDF/690aOM%20Manual%20Spec.pdf |  | OBJECTIVE: Operation and Maintenance Manuals (O&MM) – Validation Checklist
14 | Construction | Submission of draft As Constructed drawings to PAS PSS with accompanying Assurance & Validation Checklist for validation. | Draft as-constructed drawings (ASCONs) & an SDMP Assurance & Validation Checklist are provided to the PMCA / PM to confirm requirements specified in the contract and agreed EIPP delivery schedule have been met. Once these requirements are confirmed and the submission meets Defence requirements, the PMCA / PM is to sign the Checklist and forward the draft ASCONs to the PAS PSS for validation of completeness and SDMP compliance. ASCONs are to meet the following requirements: a. Drawing Format: presented in AutoCAD DWG version specified in the SDMP. b. Drawing Structure: all drawing content to be in model space, title blocks only on paper space). External references are bound to parent drawing. c. Metadata: provided with (or provision allowed for) compliant metadata taking into consideration freeform text guidance d. Revision: have been revised to final as-constructed status, remove unnecessary construction notations and labelled the title block accordingly. | Policy Spatial Data Management Plan http://www.defence.gov.au/estatemanagement/governance/Policy/SDMP/Default.asp |  | OBJECTIVE: SDMP – Validation Checklist | OBJECTIVE: Spatial Data Management Plan (SDMP)
15 | Construction | Submission of draft updated and/or new MSP and Spaces Plan to PAS PSS with accompanying Assurance & Validation Checklist for validation. | MSP. It is the Contractor’s responsibility to ensure the MSP is amended IAW SDMP to reflect all changes delivered via the project works. Spaces Plans. These differ from ASCON architectural plans and are a requirement under the SDMP. The space plans are used to create the GEMS-Geo geometries and underpin many other key datasets i.e. Fire Evacuation Plans. Space plans have defined accuracy, content and presentation requirements. An updated plan (for refurbishment projects) or provision of new plan, complying with the SDMP space plan specifications, is submitted for each building level. | Policy Spatial Data Management Plan Section 6 - Engineering Detail Survey Appendix H: Space Plan Standards http://www.defence.gov.au/estatemanagement/governance/Policy/SDMP/Default.asp |  | OBJECTIVE: Spatial Data Management Plan (SDMP) | DEFENCE.GOV:SDMP
16 | Construction | PAS review GDLs and process in EDGA. Incorrect submissions are quickly referred back to supplier with detail about issues. | PAS are to determine and agree GDL processing times that are as minimal as practical (10 working days or less) with consideration of data volumes and other PAS PSS workloads. Where errors are found, PAS PSS are to quickly advise the contractors and provide guidance about what items need to be rectified before GDLs are resubmitted by the contractor.
17 | Construction | PAS PSS feedback on draft O&MMs | PAS PSS is to conduct its primary validation of completeness and meeting O&MM Instructions, and provide feedback on the required corrective actions for the Contractor to address in the final issue O&MMs.
18 | Construction | PAS PSS feedback on draft ASCON drawings | PAS PSS is to conduct its primary validation of completeness and meeting SDMP requirements, and provide feedback on the required corrective actions for the Contractor to address in the final issue ASCONs.
19 | Construction | PAS PSS feedback on draft MSP and Spaces Plan | PAS are to confirm that new and updated MSPs, Space plans and related Metadata files comply with the SDMP.
Hand Over Take Over (HOTO)
20 | HOTO | Submission of all GDLs are delivered in accordance with the contract requirements and agreed changes implemented. | It is expected that by 28 Day notice of completion or 90% construction (depending project type), Submission of all GDLs are delivered in accordance with the contract requirements and agreed changes implemented. all estate GEMS data, including all required data fields and Warranty data would have been provided with item status updated to "In Use" to PAS PSS for validation and by HOTO, processed in EDGA. However, there will be circumstances where assets and/or defects will be identified during HOTO that require additional work or rectification. In these circumstances, the provision of remaining and/or corrected information to an agreed plan must occur. The contractor and PMCA / PM are to ensure and confirm to PAS PSS that all remaining and/or corrected estate data has been identified and will be provided to PAS PSS IAW with the agreed EIPP and provisions are in place to manage any further changes resulting during the DLP.
21 | HOTO | All final ASCON drawings and single line diagrams are delivered with agreed changes implemented. | PMCA / PM are to confirm completion of final ASCON drawings IAW the contract requirements and that changes identified and agreed from review of the "draft" drawings have been fully implemented. Once these requirements are confirmed and the submission not rejected, the PMCA / PM is to forward the final ASCONs to the PAS PSS for validation of agreed changes and uploading to Objective. Any submissions not meeting the required standards are to be returned to the Contractor for corrective action. PAS PSS are to supply a copy of all Passive Infrastructure designs to JCG.
22 | HOTO | All final O&MMs are delivered with agreed changes implemented. | PMCA / PM are to confirm completion of final O&MMs IAW the contract requirements and that changes identified and agreed from review of the "draft" O&MM have been fully implemented. Once these requirements are confirmed and the submission not rejected, the PMCA / PM is to forward the final O&MMs and accompanying assurance and validation checklist to the PAS PSS for validation of agreed changes and uploading to Objective. Any submissions not meeting the required standards are to be returned to the Contractor for corrective action.
23 | HOTO | Final updated and/or new MSP and Spaces Plan delivered with agreed changes implemented. | The contractor is to rectify issues identified by the PAS PSS and return a completed MSP and Metadata file that is compliant with the SDMP.
24 | HOTO | PAS PSS confirm all GDLs have been received, accepted and provided to the GEMS MDT for upload. | PAS PSS are to confirm that all GEMS data (excluding new items discovered/rectified during HOTO) has Asset Status updated to In Use (ZINU), applicable warranty date fields complete, data has been validated and GDLs submitted to the GEMS MDT for upload. For any outstanding GDLs or Environmental Factor Record data submissions, PAS PSS is to confirm that acceptable arrangements are in place for supply of that information and these documented in the agreed EIPP.
25 | HOTO | PAS PSS confirm all ASCON drawings received and agreed changes are complete. | PAS PSS are to review and validate that ASCONs have agreed changes implemented and non-rejected documents have been received for uploading to Objective. Any submissions not meeting the required standards are to be returned to the Contractor for corrective action IAW contract.
26 | HOTO | PAS PSS confirm all O&MM received and agreed changes are complete. | PAS PSS are to review and validate that O&M Manuals have agreed changes implemented and non-rejected documents have been received for upload. Any submissions not meeting the required standards are to be returned to the Contractor for corrective action IAW contract.
27 | HOTO | PAS PSS have reviewed and accepted Key Datasets (Mater Site Plan (MSP) and Spaces Plan) | PAS PSS are to undertake conformance checks of all returned MSP and Spaces Plans before upload, Any submissions not meeting the standards are to be returned to the Contractor for corrective action.
Defect Liability Period (DLP)
28 | DLP | GDLs submitted as a result of defect rectifications | Any GDLs that have been returned due to error are to be addressed and resubmitted. Any replacement assets or defects rectified during DLP are to be updated and the required GDL submitted IAW with the process detailed in the agreed EIPP.
29 | DLP | O&MM, ASCONs and/or MSP updated as a result of defect rectifications | Any outstanding documents\drawings that were unavailable for submission at HOTO or have been otherwise updated as a result of a rectification are to be submitted to PAS PSS for validation.
30 | DLP | PAS PSS confirm that all information submissions received for criteria 28 & 29 are compliant and suitable for uploading to the applicable Defence system. | PAS PSS are to confirm that all updated estate information provided for criteria 28 & 29 (all supplied GDLs, Drawings, O&MMs, MSPs and Metadata files, where applicable) have been validated, are compliant with the relevant Defence standards and instructions, and are loadable to the applicable Defence storage system.
Note on C22: Gavin: Add lines below to align with contractors schedule for multiple GDL delivery times.

## 8.EIPP Template
Estate Information Provision Plan Template: |  |  |  | Links
As per the Suite of Contracts, all projects must provide an Estate Information Provision Plan (EIPP). The below template is to assist contractors to understand Defence's minimum EIPP requirements and communicate these details in a simple format. Contractors are to use the provided template with additional information and topics to be added where applicable. In accordance with the conditions of contract and for the purposes of the Defence Estate Information Management, the Estate Information provision plan is to articulate how the contractor will provide, manage and govern the provision of estate data. This will be achieved via a. Setting out in adequate detail, all procedures the Contractor will implement to manage the assessment, provision, creation, recording and updating of Estate Information in accordance with the Project Contract; b. Ensuring activities detailed in the Data Provision Checklist remain aligned with the contractor’s project schedule; c.Meeting all applicable Defence Estate Information Management Requirements; d.Meeting all applicable HOTO Requirements for the provision of quality estate information. A separate EIPP plan should be prepared for both the design and construction phase of the project, unless the contractor is responsible through both stages.
Project Details - (Auto-populating from Project Details) |  |  | Comments
Project Number: | 0
Project Name: | 0
Project Location: | 0
Building/Assets Description & HOTO Descriptor: | 0
Building/Assets Number(s): | 0
Project Start Date: | 0
Project Completion Date: | 0
Key Stakeholders - (Auto-populating from Project Details) |  |  | Comments
Project Manager Contract Administrator (PMCA)
PAS Project Support Service (PSS) Representative
Contractor
Project Data Management: - Collection and Provision All key Project data management practices pertaining to the collection and provision of data required to meet Contractor Estate Information Obligations. | Design Phase | Construction Phase | Comments
Contractors must describe: by who (e.g. Internal or outsourced data supplier) and how (e.g. Web Portal, email, USB etc) data will be collected & provided to Defence, what data quality management processes are applied and list any applicable Defence and/or company data management policies or Instructions used to manage project data requirements. |  |  |  | Estate Data Management
Poject Data Security: As per the Conditions of contract, all documents, materials, media, information technology environments and all other things on or in which the Confidential Information as defined in the Suite of contracts (or any part of it) may be or is recorded, contained, set out, referred to, stored, processed or communicated (including via electronic or similar means), will be kept secure and protected at all times from all unauthorised use, access, configuration and administration. | Design Phase | Construction Phase | Comments
Contractors must describe what steps will be taken to prevent, end, avoid, mitigate or otherwise manage the adverse effect of any actual or potential Confidential Information Incident. This may include, Access controls, Data Storage location (e.g. DPN, contractor’s system), System/ Data protection (e.g. Antivirus, firewall, passwords, physical & process access controls, back-up and recovery systems etc.) and the proposed Management process for a data breach, data spill and hardware / software failure:
Project Data disposal at the end of the project: The Return, Destruction and/or Erasure of Data will be carried out in accordance with the conditions of contract and applicable Defence policies. | Design Phase | Construction Phase | Comments
Contractors must describe what action/s they will take to ensure all official information and securtiy protected assets are correctly disposed of. e.g. That in accordance with Defence requirements, all information will be deleted from corporate systems, or information pertaining to “XXX” will be retained and secured on the contractor’s corporate system and/or specified information will be returned to Defence and the remainder will be deleted from their corporate system etc. |  |  |  | Defence Security Principles Framework

## HOTO RACI
| HOTO RACI for EWP & CFI | ID Estate Planning |  | Base Manager (including Base Support team) | Zone Estate Management & Planning | Environment & Sustainability | Zone Defence Representative | Sponsor (Sustainment or Capability) Contact details listed in EIR | DG CFI (CFI projects - Accountability context is overall contract authority) | PD (Project Director - CFI projects) |  |  | Contractor (all Delivery Contractors - HC, MC & PAS) | DEWPO (EWP projects - Accountability context is overall contract authority) | PDS Project Manager - Give direction & validate compliant completion | PAS Project Manager - EWP Projects | PAS Project Support Services | PAS Project data Services - EWP and leasing Projects | PAS Manager | PAS - Electrical Operating Authority | Product Directorates | Subject Matter Experts (SME) *
(R) Responsible to do the work (delivery and/or verification or quality assurance) (A) Accountable authorities are those who are charged with making ‘the final decision’ and who have ownership of the activity or overall contract authority. (C) Consulted authorities are those who are consulted before and during the activity (I) Informed authorities are those who are informed before, during and/or at the end of the activity SME* can be but not limited to: Estate Planning, Property, Security, Fuel, Live Firing Ranges, DEEP, EO, Air Field Engineer, JCG, DS&VS, etc. |  |  | ID Engineering & Environment | [7 empty] | PMCA - CFI projects - Give direction & validate compliant completion | Design Contractor - includes DSC and "in-house" PDS. | [10 empty] | Comments:
Program Level
Capital Works Program | Development, approval and delivery of major and medium works identified in the capital works program, including the carriage of Major Works through the Parliamentary Standing Committee on Public Works | C/I | I | I | I | I | I | C | A/R | R/C |  |  |  | I |  |  | I | I | I |  | I
Estate Works Program | Planning, coordination, development and implementation of the Estate Works Program within a nationally consistent framework that is efficient and compliant with Commonwealth Procurement Guidelines. | C/I | I | I | I | I | I | C | I |  |  |  |  | A/R | R/C | R/C | I | I | I |  | I
Task/ Activity Level
Planning | Project Development and Initiation
Planning | Project start meeting held, HOTO Stakeholders identified; and Project scope & requirements, Siting Constraints, Risks identified and DLP maintenance strategy as agreed. |  |  | C | C | C | I | C |  | A | R |  | R (MC) |  | A / R | A / R | C | C |  |  | I | C / I
Planning | HOTO plan and checklist requirements identified as agreed |  |  | I | C | C | I | C |  | A | R |  | R (MC) |  | A / R | A / R | C | C |  |  |  | C / I
Design | Design
Design | Design initiation start meeting to confirm: stakeholders, scope, design and HOTO requirements. | [9 empty] | R | R |  |  | A / R | A / R | C | C | I | C |  | C | bar: I to I; R/C
Design | EIPP. Development and management of EIPP (Design phase) | [9 empty] | R | R |  |  | R | R | C | C | bar: I; R/C
Design | DPC. Development and management of DPC (Design phase) | [9 empty] | R | R |  |  | R | R | R | R | bar: I; R/C
Design | Compliant Design (includes NCC, BWM, MFPE, MIEE etc.) | [9 empty] | R | A / R | R (MC) |  | R | R | C | C | I | C |  | C | bar: I to C; R/C
Design | Approved Dispensations & Performance Solutions IAW Building Works Manual (BWM) & MIEE Policy. | I | A / R | I | I | I | I | C |  | C | C | R | C |  | C | C | C | C |  | C | I | C
Design | PAS input to Design and maintenance requirements during DLP. | [9 empty] | C / I | C |  |  | C | C | R |  | C | C | C | bar: I to I
Design | Site Selection Board Completed and Approved (National) | A / R | C | C | C | C | I | C |  | I | C | I |  |  | C | C | I | I | C | C |  | C
Design | Site Selection Board Completed and Approved (Zone) | C | C | C | R | C | A | C |  |  | C | I |  |  | R | R | I | I | C | C |  | C
Design | Building Contribution Factor completed. Applies to EWP where work relates to existing facilities | I: R; I: I; C: A / R | I | I |  |  | I | I | [6 empty] | BM responsible common areas
Design | DPC - Requirements completed (Design phase) | [9 empty] | R | R | R (MC) |  | R | R | R | R |  |  |  | C | GEMS MDT | bar: I; R/C
Pre-mobilisation | Pre-mobilisation
Pre-mobilisation | Pre-mobilisation start meeting held, key stakeholders identified, scope of works and design confirmed and Project commissioning plan, HOTO Plan & Checklist & evidence, estate information plan, schedule for O&MMs and Training all agreed by HOTO key stakeholders | [9 empty] | R |  | R |  | R | R | C | C | C |  |  | C | bar: I to I; C; R/C
Pre-mobilisation | EIPP. Development and management of EIPP (construction and DLP phases) | [9 empty] | R |  | R |  | R | R | C | C | bar: I; R/C
Pre-mobilisation | DPC. Development and management of DPC (construction and DLP phases) | [9 empty] | R |  | R |  | R | R | R | R | bar: I; R/C
Pre-mobilisation | Site Management and control plans approved by Defence. Includes: safety & incident management procedure, asbestos & hazardous chemicals management and method of Work Plans. | [9 empty] | R |  | A / R |  | R | R | C | C | C |  |  | C | bar: I to I; C; R/C
Pre-mobilisation | Dilapidation Surveys | [9 empty] | R |  | A / R |  | R | R | C | C | bar: I; R/C
Pre-mobilisation | Notification of Demolition | [9 empty] | R |  | A / R |  | R | R | C | C | I | bar: I to I; C; R/C
Pre-mobilisation | Asset Rollout Notification, Building Contribution Factor & notification of demolitions completed. Applies to all new facilities | I: C; I: C; C: R; R/C: I | R |  | C |  | R | R | C | C | I |  |  |  | Sponsor provides CF approval for new buildings.
Pre-mobilisation | Environmental approvals obtained | I: C; I: I; I: I; I: R; R/C: I | R |  | A / R |  | R | R | I | I | I
Construction | Construction
Construction | PAS confirms maintenance and support (including relevant MSPs) is ready for takeover. | [9 empty] | C |  | C |  | C | C | R | C | C |  | C | bar: I
Construction | DPC - Requirements completed (Construction phase) | [9 empty] | R |  | R |  | R | R | R | R |  |  |  | C | bar: I to I; R/C
Commissioning | Approval from the defence electrical authortity prior to energising the electrical network. | [9 empty] | R |  | A / R |  | R | R | C | C | I | R | bar: I
Commissioning | Pre-commissioning approvals and notifications completed IAW agreed contractor’s commissioning and HOTO plan. | [9 empty] | R |  | A/R |  | R | R | I | I | I | C / R |  | C / R | SME Engagement: FSB, EO, DS&VS etc where applicable. | bar: I to I; R/C
Commissioning | Training Training and “train-the-trainer” training provided by the contractor on all facility systems for the operators and maintainers; to the satisfaction of PAS and facility users. | [9 empty] | R |  | A / R |  | R | R | I | I | C | bar: I to I; C; R/C
HOTO | Hand Over Take Over (HOTO)
HOTO | Design & Build Compliance. Construction completed to approved design and all variations to original design have been approved by a certified designer. | [9 empty] | R | C | A / R |  | R | R | I | I | I | C |  | C | bar: I; I; C; R/C
HOTO | Defect Liability Period (DLP). DLP management procedure provided, maintenance plan agreed, defects list & rectification schedule provided and agreed. | [9 empty] | R |  | A / R |  | R | R | R | R | C |  | C | C | bar: I to I; C; R/C
HOTO | Property & Assets. Key schedule completed and attached with full set of tagged keys, OPE provided and building numbers & signage fixed | [9 empty] | R |  | A / R |  | R | R | C | C | C | bar: I to I; C; R/C
HOTO | Plant and Equipment. Includes criteria relating to: registerable plant, essential safety systems, Fire & smoke detection / alarm systems, and critical equipment & spares. (Criteria 5.5, 5.6, 5.9, 5.10) | [9 empty] | R |  | A / R |  | R | R | C | C | C | bar: I to I; C; R/C
HOTO | Electrical , Mechanical & Hydraulic Services. Statutory authority certificates & test certificates etc. (Criteria 5.3, 5.11, 5.13, 5.14). | [9 empty] | R |  | A / R |  | R | R | I | I | I | C/R | bar: I to I; C; R/C
HOTO | Unexploded Ordnance (UXO) certifications with maps and GPS points of boundaries clearance (plus to the required depth) | [9 empty] | R |  | A / R |  | R | R | C/I | C/I | I |  |  | C/I | EO Branch, DOTAM | bar: I to I; R/C
HOTO | Radiation safety considerations i.e. Radiation Apparatuses (removal or addition) | [9 empty] | R |  | A / R |  | R | R | C / I | C / I | I |  |  | C/I | DRSA | bar: I to I; R/C
HOTO | Emergency Evacuation Plans provided electronically and physically attached to the facilities. | I: C/I; I: I; R/C: I | R |  | A / R |  | R | R | I | I | I
HOTO | Hazardous Area and Explosives Area Verification Dossier | [9 empty] | R |  | A / R |  | R | R | C | C | I | bar: I to I; C; R/C
HOTO | List of all hazardous chemicals - quantity / type and storage system of fuels, chemicals or lubricants for uploading into ChemAlert. | [9 empty] | R |  | A / R |  | R | R | C / I | C / I | C | bar: I to I; C; R/C
HOTO | Security. Security commissioning & inspections completed and passed, access control information provided to Unit Security Officer and accreditation for Sensitive Compartmented Information Facilities (SCIF), magazines and armouries provided. (Criteria 5.15, 5.16, 5.17, 5.18, 5.19 applies) | I: C / I; I: C / I; C: C / I; R/C: I | R |  | A / R |  | R | R | C | C | I |  |  | C/R | SMEs include: Facility Certification from DS&VS, ADF ESA or ASIO-T4 (for Security Zone 5), SCEC consultants.
HOTO | Engineering & Building Management Systems. (Defence Engineering Services Network -DESN and Building Management Systems - BMS). All;equipment & networks are commissioned and connected to existing base infrastructure, testing and commissioning. | [9 empty] | R |  | A / R |  | R | R | C | C | I | C | bar: I; R/C
HOTO | Defence ICT & Voice . Defence Corporate ICT and voice passive infrastructure systems are commissioned and connected to existing base infrastructure, testing and commissioning. NOTE: JCG are only to be informed in regards to passive infrastructure and JCG are responsible for any Defence Corporate ICT active systems. (Criteria 5.21, 5.22, 5.23, 5.24 applies) | [9 empty] | R |  | A / R |  | R | R | C | C | I |  |  | C/I | JCG & Telstra | bar: I; R/C
HOTO | Billing and disconnection of services. | I: C/I; I: C/I | R |  | A / R |  | R | R | I | I |  |  | C | C/I | Energy Services PM&G Branch
HOTO | ECC Post Activity Report (PAR) Signed. | [9 empty] | R |  | A / R |  | R | R | I | I |  |  |  | C | bar: I to I; R/C
HOTO | Environment & Sustainability. ECC requirements met, land mgt plans provided, Heritage mgt plans, contaminated sites register (CSR) and smart infrastructure installed and connected. (criteria 5.27, 5.28, 5.29, 5.30, 5.31 applies) | [9 empty] | R |  | A / R |  | R | R | C | C | C |  | C | bar: I to I; R/C
HOTO | DPC. All DPC requirements have been completed. If items are incomplete and acceptance recommended, all incomplete items have been recorded in the HOTO Caveats Log and agreed to by PMCA / PM and Zone EMP rep. | [9 empty] | R |  | A / R |  | R | R | R | R |  |  |  | C | GEMS&BT | bar: I; R/C
Transition | Defence Project Transition Activities
Transition | Relevant support, services and maintenance for Base Services Contracts have been actioned and accepted by relevant service provider/s in preparation for DLP commencement. | [9 empty] | C |  | I |  | C | C | A / R | A / R | C |  | I | bar: I to C; R/C
Acceptance | Acceptance by Defence Representative that HOTO is sufficiently complete to enable Take Over. | I: I; I: C; I: I; I: A / R; C: I | C |  | C |  | C | C | C | C | I |  | I | I
DLP | Defect Liability Period (DLP)
DLP | All Defence approved HOTO caveats and issues cleared | [9 empty] | R |  | A / R |  | R | R | C | C | I | bar: I to C; R/C
DLP | NLT 28 days prior to DLP end date, all defects repaired and related estate data has been updated | [9 empty] | R |  | A / R |  | R | R | C | C | I | bar: I to C; R/C
DLP | 28 days prior to DLP end date, PAS advised and confirmed their readiness to commence agreed maintenance at the end of DLP (for CFI & by exception for EWP). | [9 empty] | C |  | C |  | C | C | A / R | A / R | C | bar: I to C; R/C
DLP | Data Provision Checklist Actions & Deliverables have been completed and verified for DLP. | [9 empty] | R |  | R |  | R | R | R | R | bar: I to I; R/C
Acceptance | Acceptance by Zone EMP Representative that DLP is complete. |  |  | I | A / R | I | I | I |  | I | C |  | C |  | R | R | C | C | I

## Abbr. & Definitions
Abbreviations and Definitions
Handover / Takeover Checklist
Abbreviations
AD EMP | Assistant Director Estate Management & Planning
AIU | Asset In Use
AP | Alternative Proposal
APZ | Asset Protection Zone
ASCON | As Constructed
ASEE | Assistant Secretary – Environment & Engineering
ASEP | Assistant Secretary - Estate Planning
AUC | Assets Under Construction
BA | Building Approval
BM | Base Manager
BMS | Base Management Systems
BSC | Base Services Contract
BSSC | Base Services Support Centre
BWM | Building Works Manual
CASG | Capability, Acquisition & Sustainment Group
CCP | Contract Change Proposal
CFI | Capital Facilities & Infrastructure
CF | Contribution Factor
CFOG | Chief Finance Officer Group
CSR | Contamination Site Register
CSRP | Critical System Recovery Plans
D&C | Design & Construct
DBSM | Directorate, Balance Sheet Management
DEEP | Directorate Estate Engineering Policy
DELM | Directorate Estate & Land Management
DEQMS | Defence Estate Quality Management System (Decommissioned 30/6/23)
DESN | Defence Engineering Service Network
DEWPO | Directorate of Estate Works Program Office
DFG | Defence Finance Group
DFI | Defence Fuel Installation
DGAA | Directorate of General Asset Accounting
DFG | Defence Finance Group
DGCFI | Director General Capital Facilities & Infrastructure
DLP | Defect Liability Period
DPC | Data Provision Checklist
DPU | Domestic Policing Unit
DRSA | Directorate of Defence Radiation Safety and Assurance
DS&VS | Defence Security & Vetting Services
DSC | Design Services Contractor
DSD | Director Service Delivery
DSPF | Defence Security Principles Framework
EBI | Estate Business Identifier
ECC | Environmental Clearance Certificate
EE Branch | Environmental & Engineering Branch
EGIS | Estate Engineering Governance & Integrity System
EEGO | Energy Efficiency in Government Operations
EAR | Environmental Assessment Report
EIPP | Estate Information Provision Plan
EISMP | Electrical Installation Safety Management Plan
EMOS | Estate Maintenance Operations Services (Decommissioned 1/2026 now PAS)
EMP | Estate Management & Planning
EO | Explosive Ordnance
EOA | Electrical Operating Authority
EPBC | Environment Protection and Biodiversity Conservation Act
ERIK | Estate Resources Information Kiosk (Decommissioned 30/6/25)
ERIM | Estate Register Information Model
ESA | Emergency Services Agency
ESD | Ecologically Sustainable Development
ESO | Environment and Sustainability Officer
EWP | Estate Works Program
FIP | Fire Indicator Panel
FSB | Fuel Services Branch
GDL | GEMS Data Load Tool
GEMS | Garrison & Estate Management System
GFE | Government Furnished Equipment
GFF | Government Furnished Facility
GPR | Ground Penetrating Radar
GPS | Global Positioning System
HC | Head Contractor
HV | High Voltage
HMAS | Her Majesties Australian Ship
HOTO | Handover / Takeover
IAW | In Accordance With
ICT | Information Communication Technology
ID | Infrastructure Division
ISM | Information Security Manual
ITP | Inspection & Test Plan
ITR | Inspection & Test Result
JCG | Joint Cabability Group
JLOG | Joint Logistics Group
MC | Managing Contractor
MEWC | Medium Estate Works Contract
MFPE | Manual of Fire Protection Engineering
MIEE | Manual of Infrastructure Engineering - Electrical
MSP | Master Site Plan
NCC | National Construction Code
NEPM | National Environment Protection Measures
NLT | No Later Than
NSIMS | National Spatial Information Management System (Decommissioning 1 FEB 26)
NSP | National Sub-metering Program
O&MM | Operation & Maintenance Manual
PABX | Private Automatic Branch Exchange
PAR | Post Activity Report
PAS | Property and Asset Services
P&E | Plant & Equipment
PD | Project Director
PM | Project Manager
PDS | Project Delivery Services
PMCA | Project Manager Contract Administrator
POC | Point of Contact
PSCCC | Physical Security Certification and Coordination Cell
PSS | Project Support Services
(Z) ESO | Zone Environment and Sustainability Officer
RACI | Responsible, Accountable, Consulted, Informed
RDMS | Resource Data Management System
RP | Registrable Plant
RSO | Range Safety Officers
RU | Resident Unit
SCADA | Supervisory Control and Data Acquisition
SCEC | Security Construction & Equipment Committee
SCIF | Sensitive Compartmented Information Facilities
SDD | Service Delivery Division
SDMP | Spatial Data Management Plan
SEG | Security & Estate Group
SERS | Safety Environment Reporting System
SI | Standing Instructions
SME | Subject Matter Experts
SOP | Standard Operating Procedures
SSMP | Site Safety Management Plan
UXO | Unexploded Ordnance
WHS | Work Health and Safety
WOL | Whole-of-Life
Definitions
Acceptance of Delivered Works | A term whereby the Zone Defence Representative or authorised delegate accepts the delivered works into the Defence estate. The Acceptance is confirmed by the Defence Representative being satisfied that all deliverables are met, satisfactorily completed, fit for purpose, Defence estate information requirements are met and signing the completed HOTO Checklist to that effect.
Base Services Contractor | The incumbent Contractor, contracted by Defence to provide base services including estate upkeep, cleaning etc.
Caveat | A caveat is a notice or warning issued by Defence. The caveat can be issued by the Defence Representative (Zone DSD or authorised delegate) indicating the conditional acceptance by Defence that HOTO criteria can be met within an acceptable period of time post HOTO (within DLP). Caveats will be assessed on their associated risks and must be approved by the Defence Representative.
Commonwealth's Representative. | The person nominated in the Contract Particulars or any other person nominated by the Commonwealth, For CFI projects this is generally the Project Director (PD) who will give direction to the PMCA.
Condition Assessment | An inspection of all plant and equipment maintained under the service to determine its capacity to meet the required outputs and identify obvious condition related issues.
Contractor | The Contractor who is the signatory to the contract. The entity that has been engaged to design and/ or deliver the works. The Designer, Head Contractor and Managing Contractors are responsible for developing the Project Lifecycle & HOTO pLan and DPC; and demonstrating that designs are compliant (for Designer) and that all deliverables are satisfactorily completed, safe, fit for purpose and Defence specified estate information requirements are met.
Contract Deliverable not Provided | A contract deliverable not provided by the contracted entity responsible at the required time.
Defect | A defect is a fault, imperfection (including shrinkage) or deficiency (or omission) in delivered works: something not to the required standard. The defect is to be corrected by the contractor representative.
Defence Representative (DR) | The Defence Representative (Zone Director Service Delivery (DSD) or authorised delegate (e.g. Zone AD EMP) is responsible for Takeover (TO) or accepting the delivered works from the Commonwealth Representative (CFI projects - Project Director) and/or PMs, for ongoing sustainment by SDD and Base Services Contractors and enabling its use by the RU for its intended purpose. The acceptance is confirmed by the Defence Representative being satisfied that all project deliverables are satisfactorily completed, are safe and fit for purpose, Defence estate information requirements are met, incomplete or defective works have an acceptable remediation plan and signing the completed HOTO Plan & Checklist to that effect.
Delivered Works | Relates to the entire scope of works delivered under the contract. The delivered works include all scope changes, variations, physical works, documentation, electronic system and data.
Estate Appraisal | A program of physical inspections, condition assessments and desktop reviews of Defence facilities, infrastructure, plant and equipment to assess the gap between target condition and functionality criteria and assessed condition and functionality.
Handover Process | A term whereby the PD / PM accepts the completed works from the Contractor as satisfactorily completed, safe and fit for purpose and ready for presentation to the Defence Representative and ultimately acceptance by Defence.
Issue | A matter to be resolved by Defence and the project contractor representative(s).
Project Completion | A term whereby the PMCA / PM accepts the completed works from the Contractor as satisfactorily completed, safe and fit for purpose and issues a completion notice of letter.
Project Director (PD) | An appointment generally applying to CFI projects as the person representing the Commonwealth's (Defence) requirements, who has the overall responsibility to ensure the conduct of project planning, design, execution, monitoring, controlling and closure are successfully performed by contracted entities.
Project Manager (PM) | The appointed manager or consultant that represents the Commonwealth's (Defence) requirements for project delivery. For Estate Works Program this roll is generally performed by the PDS contractor, however the roll can be performed by a PM for PAS project delivery services or other Groups & Services delivered projects. PMs have the overall responsibility to ensure the conduct of project planning, design, execution, monitoring, controlling and closure are successfully performed IAW contract, policy and legislative requirements.
Project Manager Contract Administrator (PMCA) | The PMCA "consultants" are engaged to give directions and carry out all of the other functions under the PMCA services contract and project contract as the agent of the Commonwealth.
Responsible Person | The term Responsible Person within this checklist identifies the person who is responsible for delivery of an individual item. The Contractor Representative identifies the individual by position or name within the checklists column of “Responsible Person / Position Title”.
Stakeholder | A stakeholder is any individual, group or organisation that can affect, be affected by, or perceived to be affected by a project. Stakeholder inclusion is a critical component to the successful delivery of any project.
Takeover Process | A process whereby the Defence Representative commences the evidentiary assessment for the purpose of accepting the delivered works from the PD or PM as satisfactorily completed, safe and fit for purpose.
Train the Trainer | The trainer provides training to selected staff that becomes the trainer for all other staff.
Zone EMP Representative | Zone Estate Management & Planning (EMP) Representatives are responsible to contribute to key project activities, identify and raise project issues to the PMCA / PM or PD for resolution and ensure appropriate SDD support is provided throughout the project lifecycle. At HOTO, the Zone EMP representative validates the HOTO checklist once completed by the PMCA / PM; and prepares the HOTO submission and recommendation for SDD Take Over (TO) to the Defence Representative.

## Reference Cells (hidden)
Target: | EWP/ PMB output | CFI & Other output | EWP/ PMB output | CFI & Other output
Sheet 2, Row 7 Item 1 | Project start meeting held where key Stakeholders are identified and Project HOTO requirements are discussed and confirmed including:- - Clarification of Project Scope - Provision of Baseline Project Schedule | Project start meeting held where key Stakeholders are identified and Project HOTO requirements are discussed and confirmed including:- - Clarification of Project Scope - Provision of Baseline Project Schedule - Access provided to project web based document management systems | A copy of the project start meeting minutes. If not addressed in the minutes, also provide a copy of: * List of key project stakeholders and their ongoing role / required meeting requirements. *Acknowledgement that key stakeholders received & agree (where applicable) the project scope of works. *Provision of approved Phase Report / Return Brief. *Baseline Project Schedule | A copy of the project start meeting minutes. If not addressed in the minutes, also provide a copy of: * List of key project stakeholders and their ongoing role / required meeting requirements. *Acknowledgement that key stakeholders received & agree (where applicable) the project scope of works. *Copy of IBC or DBC authorities page. *Baseline Project Schedule * An email from the PMCA / PM advising data system access arrangements and list of stakeholders provided access .
Sheet 7, Row 5 Item 1 | Estate Data provided to Designer (required for existing facilities, extending current infrastructure and/or upgrading existing assets) | Data Extracts from GEMS provided to Designer (required for existing facilities, extending current infrastructure and/or upgrading existing assets) | Data extracts are to be taken to inform the design process and also identify what information will require updating as a result of the project. Extracts should be used "for information only" purposes as GEMS data can be incomplete and/or inaccurate. If after inspection of the GEMS data extracts it is found that data is missing or incorrect, and it inhibits the PAS Data Service from creating project related asset shell and data records via GDLs (e.g. where a functional parent is required but extracted data is missing or incorrect). PAS Data Services is to create new shell and data records via GDL submission to address the problem. Where missing or incorrect data is identified but does not inhibit the project data creation requirements, PAS are to initiate remedial action. Spaces Plan. Where a spaces plan is available for an existing facility, PAS is to provide a copy for project to reference. PAS Data Services to create/ update spaces plans as applicable. | Data extracts are to be taken to inform the design process and also identify what information will require updating as a result of the project. (Extracts should be used "for information only" purposes as GEMS data can be incomplete and/or inaccurate. Requests for these extracts are to be prepared using the Request Estate Data Form, to define the scale and extent of data to be included. The form can be obtained from the Estate Data Management "Forms" Objective link. If unsure of the extent of the current estate data, liaise with PAS PSS to ensure correct footprint is requested If after inspection of the GEMS data extracts it is found that data is missing or incorrect, and it inhibits the contractor from creating project related asset shell and data records via GDLs (e.g. where a functional parent is required but extracted data is missing or incorrect) the contractor is to create new shell and data records via GDL submission to address the problem. Where missing or incorrect data does not inhibit the project data creation requirements, PMCAs / PMs are to report the data anomalies to PAS PSS to initiate remedial action. Spaces Plan. Where a spaces plan is available for an existing facility, PAS is to provide a copy for project to reference and/or update as applicable. For a new facility the project is to create and provide a spaces plan for the facility.
Sheet 7, Row 6 Item 2 | The project provides preliminary data necessary to enable PAS Data Service to create asset shell records for Buildings, Levels, Spaces, Infrastructure, Equipment Systems & Equipment (where known) etc. and provides a new or updated spaces plan. | The Project submits a GDL to PAS PSS requesting to create asset shell records for Buildings, Levels, Spaces, Infrastructure, Equipment Systems & Equipment (where known) etc. and provides a new or updated spaces plan. GDL and Spatial Data submissions are accompanied by relevant Assurance & Validation Checklists | Asset shell records are the minimum data attributes required to create an initial record in the GEMS database that can be added to later and are created using the GDL. The preliminary data required for creation of initial records is to be identified through a collaborative engagement between the PMCA and PSS. This data may include: Asset details, Qty, physical location etc. GDLs are to be completed to request asset shell creation for all new assets using the endorsed Data Requirements documentation (Estate Class Mapping Diagrams for all Estate Classes, EBI Numbering Plan for Levels and Spaces). This is done early in the project lifecycle to ensure all dependant activities are founded on accurate shell records to reduce latter complications. Completed GDL requests are submitted to GEMS for processing. It may be beneficial for projects to request the creation of shell records for building assets earlier in the design phase once it is known how many new buildings may be required to ease the integration of EBIs into drawing Title block information. Note: creating new asset shells relates to shell records for Building, Level, Space, Infrastructure, Equipment and Equipment Systems where these are known in the design phase. | Asset shell records are the minimum data attributes required to create an initial record in the GEMS database that can be added to later and are created using the GDL. GDLs are to be completed to request asset shell creation for all new assets using the endorsed Data Requirements documentation (Estate Class Mapping Diagrams for all Estate Classes, EBI Numbering Plan for Levels and Spaces). This is done early in the project lifecycle to ensure all dependant activities are founded on accurate shell records to reduce latter complications. Completed GDL requests are submitted to GEMS for processing. It may be beneficial for projects to request the creation of shell records for building assets earlier in the design phase once it is known how many new buildings may be required to ease the integration of EBIs into drawing Title block information. Note: creating new asset shells relates to shell records for Building, Level, Space, Infrastructure, Equipment and Equipment Systems where these are known in the design phase.
Sheet 7, Row 7 Item 3 | GDLs processed in EDGA. | PAS review GDLs and process in EDGA. Incorrect submissions are quickly referred back to supplier with detail about issues.
Sheet 7, Row 8 Item 4 | All GDLs shell records have been created by PAS Data Service by the 90% design - Building, Level, Space, Infrastructure, Equipment Systems & Equipment (where known) etc. | All required GDLs to create shell records have been submitted to PAS PSS by the 90% design - Building, Level, Space, Infrastructure, Equipment Systems & Equipment (where known) etc.
Sheet 7, Row 10 Item 6 | Spaces Plan prepared IAW SDMP | Spaces Plan prepared IAW SDMP and submitted with completed SDMP Assurance & Validation Checklist.
Sheet 7, Row 12 Item 7 | Estate Data provided to Contractor Representative (required for existing facilities, extending current infrastructure and/or upgrading existing) | Data Extracts from GEMS provided to Contractor Representative (required for existing facilities, extending current infrastructure and/or upgrading existing) | Data extracts are to be taken to inform the ongoing development, update and submission of estate data throughout the construction phase. Liaise with PAS to ensure correct footprint is requested. If the data extracts are missing data or the data provided is incorrect, after inspection, take measures to have these records corrected/updated/created. Contact the PAS, who will manage accordingly. | Data extracts are to be taken to inform the ongoing development, update and submission of GDLs throughout the construction phase. Requests for extracts is via use of the Request Estate Data Form obtained from the Defence Estate Information Page. If unsure of the extent of the current estate data, liaise with PAS to ensure correct footprint is requested. If the GEMS data extracts are missing data or the data provided is incorrect, after inspection, take measures to have these records corrected/updated/created. Contact the PAS, who will be able to guide the data supplier in the right direction to have this missing data created or incorrect data updated.
Sheet 7, Row 13 Item 8 | PAS Data Service Create asset shell records and / or Update asset records | The Project submits GDLs with completedAssurance & Validation Checklist to PAS PSS requesting to Create asset shell records and / or Update asset records. Incorrect submissions are quickly referred back to supplier with detail about issue areas. | Large projects by nature are required to submit considerable amounts of data. The larger the project, the larger amount of information will be created. To avoid processing issues, reviewing and approving an entire project set of data can create unnecessary delays or other issues. Data submissions are to be broken down into logical batches where appropriate. For large and/or complex projects, incremental or a rolling provision of data could be expected from early in the construction phase to 90% construction or 28 day notice of completion. If there have been any changes made to the design, check with the GEMS MDT to ensure that current shell records are consistent with the design change. If they are no longer accurate, advise the PAS Project Data Service of the changes/updates/deletions to be made. GDLs must take into account any updates (either New Asset or Disposal\Demolition) that have occurred over the period. These data submissions should also include any submissions or updates to hazards or asbestos data and any necessary environmental data using the appropriate EFR GDL. A GDL submission/ Data supply schedule is to be developed, agreed and circulated to representatives at the commencement of the Construction Phase and forms part of the EIPP. Where the provision and/or upload of GDL's/or data required for their creation, is incomplete, the PMCA / PM, PAS PSS, the Zone EMP rep and contractor are to revise the EIPP and agree to a new data supply schedule as required. When loading the initial Update GDL, DLP dates are to reflect the completion date programmed at the time of submission, noting that this date may change as the project nears completion. Should the completion date nominated in the initial Update GDL differ at the time of project completion, the final Update GDL is to capture these changes and the DLP dates are modified to reflect the accurate dates. If the final GDL has been loaded prior to the accurate DLP dates being known, the PAS must update when when DLP dates are confirmed . | Large projects by nature are required to submit considerable amounts of data. The larger the project, the larger amount of information will be created. To avoid processing issues, reviewing and approving an entire project set of data can create unnecessary delays or other issues. Data submissions are to be broken down into logical batches where appropriate. For large and/or complex projects, incremental or a rolling provision of data could be expected from early in the construction phase to 90% construction or 28 day notice of completion. All GDL Submissions must be accompanied by an Assurance and Validation Checklist, a single Checklist may be used for multiple GDL's when submitted at the same time. If there have been any changes made to the design, check with the GEMS MDT to ensure that current shell records are consistent with the design change. If they are no longer accurate, create new shells records in a new GDL and advise PAS PSS & GEMS MDT of the changes/updates/deletions to be made. GDLs must take into account any updates (either New Asset or Disposal\Demolition) that have occurred over the period. These data submissions should also include any submissions or updates to hazards or asbestos data and any necessary environmental data using the appropriate EFR GDL. A GDL submission schedule is to be developed, agreed and circulated to representatives at the commencement of the Construction Phase and forms part of the EIPP. Where the provision and/or upload of GDLs is incomplete, the PMCA / PM, PAS PSS, the Zone EMP rep and contractor are to revise the EIPP and agree to a new data supply schedule as required. When submitting the initial Update GDL, the contractor is to ensure the DLP dates reflect the completion date programmed at the time of submission, noting that this date may change as the project nears completion. Should the completion date nominated in the initial Update GDL differ at the time of project completion, the contractor is to ensure that the final Update GDL captures these changes and the DLP dates are modified to reflect the accurate dates. If the final GDL has been accepted prior to the accurate DLP dates being known, and provided there are no other changes required, the contractor is to inform the PAS. In this situation the PAS will perform the update of the DLP dates.
Sheet 7, Row 14 Item 9 | Additional GDL create/updates, as required & determined by project. (all data for new or updated items is to be supplied to PAS Data Service for GDL creation and upload by 90% construction). | Additional GDL submissions, as required & determined by project. (all data for new or updated items is to be supplied via GDL by 90% construction). | Additional rows are added to the checklist to record the different batches and timing of GDL's . For large projects there may be many batches that align to project construction phase, as different facilities and/or assets are completed etc. | Additional rows are added to the checklist to record the different batches and timing of GDL submissions to PAS. For large projects there may be many batches that align to project construction phase, as different facilities and/or assets are completed etc.
Sheet 7, Row 14 Item 10 | GDLs process in EDGA. | PAS review GDLs and process in EDGA. Incorrect submissions are quickly referred back to supplier with detail about issues | With consideration of the contractor's proposed Data submission schedule, PAS are to determine and agree GDL Creation and processing times that are as minimal as practical. | With consideration of the contractor's proposed GDL submission schedule, PAS PSS are to determine and agree GDL processing times that are as minimal as practical (10 working days or less with consideration of data volumes and other PAS PSS workloads). Where errors are found, PAS PSS are to quickly advise the contractors and provide guidance about what items need to be rectified before GDLs are resubmitted by the contractor representative.
Sheet 7, Row 16 Item 11 | Project advises PAS of required changes and provides relevant data to PAS to update the Master Site Plan (MSP). | RFI Notice to request Master Site Plan (MSP) for Update purposes issued to PAS PSS. | Master Site Plans (MSP) are controlled access documents and can only be issued to one party at a time for update and will only be issued for the minimum length of time to conduct the update. PAS Project Data Service are required to update this plan IAW the SDMP. To ensure PAS Project Data Services are able to update MSP in a timely manner, projects are to:: a. familiarise themselves with the content\accuracy requirements of the SDMP; b. collect by means of survey to satisfy accuracy provisions, all changes to the estate from the building line out. Updates to the MSP generally can occur once all major construction and landscaping works external to the building line are complete. Requesting this plan when this criteria is met may allow additional flexibility in the provision timeline in event the document is unavailable. Note: This can be initiated earlier in the process than construction, to allow for more efficient planning and management of the requirement/s, enabling validation by or before HOTO. | Master Site Plans (MSP) are controlled access documents and can only be issued to one party at a time for update and will only be issued for the minimum length of time to conduct the update. Projects are required to update this plan IAW the SDMP. Projects are to: a. familiarise themselves with the content\accuracy and submission requirements of the SDMP; b. submit a request to obtain a MSP once all major external works are completed; and c. collect by means of survey to satisfy accuracy provisions, all changes to the estate from the building line out. Updates to the MSP generally can occur once all major construction and landscaping works external to the building line are complete. Requesting this plan when this criteria is met may allow additional flexibility in the provision timeline in event the document is unavailable. Note: This can be initiated earlier in the process than construction, to allow for more efficient planning and management of the requirement/s, enabling validation by or before HOTO.
Sheet 7, Row 18 Item 12 | Upload of all GDLs with required data fields complete. | Submission of all GDLs with accompanying GDL Assurance & Validation Checklist to PAS PSS - all data fields completed. | By this stage, all GDLs should have been completed (including necessary asset attributes). PAS Project Data Service are to engage with the contractor/ designer for supply of all raw project data necessary to populate GDL's. | By this stage, all GDLs should have been completed (including necessary asset attributes) and submitted to the PAS PSS for review, validation and upload.
Sheet 7, Row 19 Item 13 | Draft O&MM loaded to project objective folder. | Submission of draft O&MM with accompanying O&MM Assurance & Validation Checklist for validation. | Contractor, PMCA / PM and PAS to confirm requirements specified in the contract and agreed EIPP delivery schedule. Once these requirements are confirmed PAS Project Data Service develop and/or update the draft O&MMs in accordance with Defence O&MM Instructions. All O&MMs by this stage need to be prepared and submitted (either as draft digital media or notified draft completion for Online Document management system). O&MMs content to be confirmed with the Contractor to ensure all relevant content has been provided and completeness of all project relevant sections as required IAW the Defence O&MM Instructions. | Draft O&MMs are provided to the PMCA / PM to confirm requirements specified in the contract and agreed EIPP delivery schedule have been met. Once these requirements are confirmed and the submission checked, the PMCA / PM is to forward the draft O&MMs to the PAS PSS for validation of completeness and meeting Defence O&MM Instructions. All O&MMs by this stage need to be prepared and submitted to review (either as draft digital media or notified draft completion for Online Document management system). O&MMs are to be checked and quality assured by the Contractor prior to submission to ensure all relevant content has been provided and completeness of all project relevant sections as required IAW the Defence O&MM Instructions. An Assurance & Validation Checklist is to be completed as part of this process.
Sheet 7, Row 21 Item 15 | Draft updated and/or new MSP and Spaces Plan created by PAS Project Data Service. | Submission of draft updated and/or new MSP and Spaces Plan to PAS PSS with accompanying Assurance & Validation Checklist for validation. | MSP. It is the Contractor’s responsibility to supply the PAS Project Data Service with all required project data to enable PAS to Develop and/or update MSP’s IAW the SDMP to reflect all changes delivered via the project works. Spaces Plans. These differ from ASCON architectural plans and are a requirement under the SDMP. The space plans are used to create the GEMS-Geo geometries and underpin many other key datasets i.e. Fire Evacuation Plans. Space plans have defined accuracy, content and presentation requirements. Contractor’s are to supply the PAS Project Data Service with all required project data to enable PAS to update space plans (for refurbishment projects) or create new plans, complying with the SDMP space plan specifications, for each building level. | MSP. It is the Contractor’s responsibility to ensure the MSP is amended IAW SDMP to reflect all changes delivered via the project works. Spaces Plans. These differ from ASCON architectural plans and are a requirement under the SDMP. The space plans are used to create the GEMS-Geo geometries and underpin many other key datasets i.e. Fire Evacuation Plans. Space plans have defined accuracy, content and presentation requirements. An updated plan (for refurbishment projects) or provision of new plan, complying with the SDMP space plan specifications, is submitted for each building level.
Sheet 7, Row 22 Item 16 | GDL's processed in EDGA. | PAS review GDLs and process in EDGA. Incorrect submissions are quickly referred back to supplier with detail about issues. | PAS are to advise GDL processing times. | PAS are to determine and agree GDL processing times that are as minimal as practical (10 working days or less) with consideration of data volumes and other PAS PSS workloads. Where errors are found, PAS PSS are to quickly advise the contractors and provide guidance about what items need to be rectified before GDLs are resubmitted by the contractor.
Sheet 7, Row 23 Item 17 | Final O&MM update activities identified. | PAS PSS feedback on draft O&MMs | PAS project data service confirm outstanding contractor actions for final issue O&MMs. | PAS PSS is to conduct its primary validation of completeness and meeting O&MM Instructions, and provide feedback on the required corrective actions for the Contractor to address in the final issue O&MMs.
Sheet 7, Row 25 Item 19 | Final MSP and Spaces Plan update activities identified. | PAS PSS feedback on draft MSP and Spaces Plan | PAS project data service confirm outstanding contractor actions required for MSPs and Space plans updates. | PAS are to confirm that new and updated MSPs, Space plans and related Metadata files comply with the SDMP.
Sheet 7, Row 27 Item 20 |  |  | It is expected that by 90% construction, all estate GEMS data, including all required data fields and Warranty data would have been processed in EDGA with item status updated to "In Use" . However, there will be circumstances where assets and/or defects will be identified during HOTO that require additional work or rectification. In these circumstances, the provision of remaining and/or corrected information to an agreed plan must occur. The contractor and PAS Project Data Service are to ensure all required project data is supplied for GDL updates and all remaining and/or corrected estate data has been identified and will be provided to IAW with the agreed EIPP. The contractor and PMCA / PM to confirm provisions are in place to manage any further changes resulting during the DLP. | It is expected that by 28 Day notice of completion or 90% construction (depending project type), Submission of all GDLs are delivered in accordance with the contract requirements and agreed changes implemented. all estate GEMS data, including all required data fields and Warranty data would have been provided with item status updated to "In Use" to PAS PSS for validation and by HOTO, processed in EDGA. However, there will be circumstances where assets and/or defects will be identified during HOTO that require additional work or rectification. In these circumstances, the provision of remaining and/or corrected information to an agreed plan must occur. The contractor and PMCA / PM are to ensure and confirm to PAS PSS that all remaining and/or corrected estate data has been identified and will be provided to PAS PSS IAW with the agreed EIPP and provisions are in place to manage any further changes resulting during the DLP.
Sheet 7, Row 29 Item 22 |  |  | Final O&MMs can be uploaded to Objective. | PMCA / PM are to confirm completion of final O&MMs IAW the contract requirements and that changes identified and agreed from review of the "draft" O&MM have been fully implemented. Once these requirements are confirmed and the submission not rejected, the PMCA / PM is to forward the final O&MMs and accompanying assurance and validation checklist to the PAS PSS for validation of agreed changes and uploading to Objective. Any submissions not meeting the required standards are to be returned to the Contractor for corrective action.
Sheet 7, Row 30 Item 23 |  |  | Final updated and/or new MSP and Spaces Plan delivered . | The contractor is to rectify issues identified by the PAS PSS and return a completed MSP and Metadata file that is compliant with the SDMP.
Sheet 7, Row 31 Item 24 | All GDLs have been processed in EDGA | PAS PSS confirm all GDLs have been received, accepted and provided to the GEMS MDT for upload. | All GEMS data (excluding new items discovered/rectified during HOTO) has Asset Status updated to In Use (ZINU), applicable warranty date fields complete, data has been validated and GDLs processed in EDGA . For any outstanding GDLs or Environmental Factor Record data submissions, PAS is to confirm that acceptable arrangements are in place for supply of that information and these documented in the agreed EIPP. | PAS PSS are to confirm that all GEMS data (excluding new items discovered/rectified during HOTO) has Asset Status updated to In Use (ZINU), applicable warranty date fields complete, data has been validated and GDLs submitted to the GEMS MDT for upload. For any outstanding GDLs or Environmental Factor Record data submissions, PAS PSS is to confirm that acceptable arrangements are in place for supply of that information and these documented in the agreed EIPP.
Sheet 7, Row 33 Item 26 | N/A | PAS PSS confirm all O&MM received and agreed changes are complete. | N/A | PAS PSS are to review and validate that O&M Manuals have agreed changes implemented and non-rejected documents have been received for upload. Any submissions not meeting the required standards are to be returned to the Contractor for corrective action IAW contract.
Sheet 7, Row 34 Item 27 | Key Datasets (Mater Site Plan (MSP) and Spaces Plan) upladed | PAS PSS have reviewed and accepted Key Datasets (Mater Site Plan (MSP) and Spaces Plan) | MSP and Spaces Plans uploaded in accordance with the SEG Records Management Contractor Guide. a. Spatial data (including spatial GDL outputs and GIS layers) must be managed via the Estate Geospatial System. b.Related non- spatial data (As Constructed drawings, DWG Master Site Plans, O&M Manuals, reports, PDFs) must be stored in Objective. | PAS PSS are to undertake conformance checks of all returned MSP and Spaces Plans before upload, Any submissions not meeting the standards are to be returned to the Contractor for corrective action.
Sheet 7, Row 38 Item 30 | PAS PSS confirm that ASCONS are compliant and suitable for uploading to the applicable Defence system. | PAS PSS confirm that all information submissions received for criteria 28 & 29 are compliant and suitable for uploading to the applicable Defence system. | PAS PSS are to confirm ASCONS have been validated, are compliant with the relevant Defence standards and instructions, and are loadable to the applicable Defence storage system. | PAS PSS are to confirm that all updated estate information provided for criteria 28 & 29 (all supplied GDLs, Drawings, O&MMs, MSPs and Metadata files, where applicable) have been validated, are compliant with the relevant Defence standards and instructions, and are loadable to the applicable Defence storage system.
Sheet 6, Row 8 Item 2.0 |  |  | Throughout the project design phase there may be several meetings and various activities conducted to ensure the required stakeholders are engaged, project scope and deliverables (including approved changes) are understood & agreed; risks and constraints are identified; and plans, designs and drawings are developed to the required standards. Design initiation start meeting. Must be held at the commencement of the design phase. The PMCA / PM are to ensure that all appropriate stakeholders are identified and represented for the meeting. Items that should be addressed at the design start meeting may include but not be limited to: a. All applicable stakeholders and SME for the design phase activities have been identified and engaged. b. Project scope, schedule and deliverables are clearly understood and agreed to by key stakeholders. c. Site risks, constraints, environmental management and renewable energy requirements identified. d. The HOTO Plan & Checklist for the design deliverables is reviewed, acceptance criteria and completion evidence are agreed. e. An Estate Information Provision Plan (EIPP) & Data Provision checklist (DPC) for the supply and management of estate information has been reviewed and agreed. The EIPP should cover provision of GEMS data, estate data extracts, drawings and geo-data etc. f. PMCA / PM arranging Estate Data extracts for all existing infrastructure, buildings and equipment affected by the project works. Requests for these extracts are to be prepared using the Request Estate Data Form, to define the scale and extent of data to be included. g. Ensuring that PAS specialist maintenance advice is provided during the design process. The PAS are able to provide maintenance advice for buildings, infrastructure, plant & equipment and land management requirements. h. Base access arrangements for visitors etc. i. Explain PAS PSS services, clarify notice and return times for estate data and RFIs. Where available PAS are to provide contractors an information pack about PAS PSS services. j.Explain PAS Project Data Service. Clarify contractor project data supply requirement and PAS Project Data Service estate data creation/ update deliverables and time frames. k. Where a Design includes installation of a renewable energy supply please liaise with DERMS. email: Smart.infrastructure@defence.gov.au l.EGIS Product Report (EPR) and EGIS Advice Register (EAR) creation, storage and usage requirements are understood. Relevant Policy Owners are notified of Project’s EAR Objective location for their future use. Larger and more complex designs generally have design milestones established at 30%, 50% and 90%, with corresponding design review meetings. The contractor and PMCA / PM must ensure applicable stakeholders and SME have been adequately engaged to provide input at agreed project design review milestones and/or meetings. | Throughout the project design phase there may be several meetings and various activities conducted to ensure the required stakeholders are engaged, project scope and deliverables (including approved changes) are understood & agreed; risks and constraints are identified; and plans, designs and drawings are developed to the required standards. Design initiation start meeting. Must be held at the commencement of the design phase. The PMCA / PM are to ensure that all appropriate stakeholders are identified and represented for the meeting. Items that should be addressed at the design start meeting may include but not be limited to: a. All applicable stakeholders and SME for the design phase activities have been identified and engaged. b. Project scope, schedule and deliverables are clearly understood and agreed to by key stakeholders. c. Site risks, constraints, environmental management and renewable energy requirements identified. d. The HOTO Plan & Checklist for the design deliverables is reviewed, acceptance criteria and completion evidence are agreed. e. An Estate Information Provision Plan (EIPP) & Data Provision checklist (DPC) for the supply and management of estate information has been reviewed and agreed. The EIPP should cover provision of GEMS data, estate data extracts, drawings and geo-data etc. f. PMCA / PM arranging Estate Data extracts for all existing infrastructure, buildings and equipment affected by the project works. Requests for these extracts are to be prepared using the Request Estate Data Form, to define the scale and extent of data to be included. g. Ensuring that PAS specialist maintenance advice is provided during the design process. The PAS are able to provide maintenance advice for buildings, infrastructure, plant & equipment and land management requirements. h. Base access arrangements for visitors etc. i. Explain PAS PSS services, clarify notice and return times for estate data and RFIs. Where available PAS are to provide contractors an information pack about PAS PSS services. j. Where a Design includes installation of a renewable energy supply please liaise with DERMS. email: Smart.infrastructure@defence.gov.au k.EGIS Product Report (EPR) and EGIS Advice Register (EAR) creation, storage and usage requirements are understood. Relevant Policy Owners are notified of Project’s EAR Objective location for their future use. Larger and more complex designs generally have design milestones established at 30%, 50% and 90%, with corresponding design review meetings. The contractor and PMCA / PM must ensure applicable stakeholders and SME have been adequately engaged to provide input at agreed project design review milestones and/or meetings.
Sheet 6, Row 9 Item 2.1 |  |  | Contractor (designer) is required to develop a Estate Information Provision Plan (EIPP) in coordination with PAS Project Data service that details what, how, who and when estate data associated with the project will be managed and provided to Defence. The EIPP must cover management and delivery arrangements for all forms of new and changed estate data that is defined by the Estate Register Information Model (ERIM), environmental and estate related registers, project plans, drawings and manuals etc. Where PAS Project data service are responsible for Estate Data creation/update, the EIPP & DPC shall include details of necessary project data to be supplied by the contractor to PAS Project Data Service and estimated creation timeframes. The EIPP must accord with applicable Defence policies, business rules and manuals to ensure the conditions of the contract are met and provision & acceptance of quality data is achieved at the required project phases. When developing the EIPP and Data Provision Checklist (DPC) , contractors must liaise with PMCA / PM, PAS PSS and PAS Project Data Service to ensure associated processes are understood and planned data supply and verification schedules can be achieved. Refer to the EIPP Template (tab 8) for further information about EIPP requirements. Refer to the Data Provision Checklist (tab 3) and data provision checklist Inst (tab 7) in this HOTO Plan and checklist document for further information about DPC requirements. Note: Design services contractors only need to complete an EIPP and select applicable DPC criteria listed in the design phase. | Contractor (designer) is required to develop a Estate Information Provision Plan (EIPP) that details what, how, who and when estate data associated with the project will be managed and provided to Defence. The EIPP must cover management and delivery arrangements for all forms of new and changed estate data that is defined by the Estate Register Information Model (ERIM), environmental and estate related registers, project plans, drawings and manuals etc. The EIPP must accord with applicable Defence policies, business rules and manuals to ensure the conditions of the contract are met and provision & acceptance of quality data is achieved at the required project phases. When developing the EIPP and Data Provision Checklist (DPC) , contractors must liaise with PMCA / PM and PAS PSS to ensure associated processes are understood and planned data supply and verification schedules can be achieved. Refer to the EIPP Template (tab 8) for further information about EIPP requirements. Refer to the Data Provision Checklist (tab 3) and data provision checklist Inst (tab 7) in this HOTO Plan and checklist document for further information about DPC requirements. Note: Design services contractors only need to complete an EIPP and select applicable DPC criteria listed in the design phase.
Sheet 6, Row 34 Item 4.2 |  |  | Where a Data Provision Checklist (DPC) is established and agreed at the commencement of the construction phase, DPC actions and deliverables are to be regularly reviewed and completed as early as practical. This criteria is met once the agreed construction phase actions and deliverables have been completed. Refer to the PDC and DPC Inst tabs in the HOTO Plan and checklist document for further information about DPC requirements. The contractor is responsible for ensuring the accuracy and timeliness of all project data required for the creation of estate data. The contractor must also develop an Estate Information Provision Plan (EIPP) and a Data Provisioning Checklist (DPC) in coordination with the PAS Project Data Service that outlines how and when all project data required for GDL creation update will be provided to PAS to enable validation by 90% construction or 28 days prior to notice of completion (as applicable and agreed). | Where a Data Provision Checklist (DPC) is established and agreed at the commencement of the construction phase, DPC actions and deliverables are to be regularly reviewed and completed as early as practical. This criteria is met once the agreed construction phase actions and deliverables have been completed. Refer to the PDC and DPC Inst tabs in the HOTO Plan and checklist document for further information about DPC requirements. The contractor is responsible for the accuracy, completeness and timeliness of all estate information created or amended by the project. The contract is also responsible to develop Estate Information Provision Plan (EIPP) & DPC that outlines how and when all GDL will be provided to PAS for validation by 90% construction or 28 days prior to notice of completion (as applicable and agreed).
Sheet 6, Row 86 Item 6.3 |  |  | It is expected that by HOTO, all Estate Data has been provided, validated for accuracy / completeness and GDL proved to PAS PSS. However there will be circumstances where items and/or defects will be identified during HOTO and DLP that require additional work or rectification. In these circumstances, the provision of remaining and/or corrected information to an agreed plan will occur. The contractor and PAS Project Data Service are to ensure and confirm to PAS PSS that all remaining and/or corrected estate data has been provided and saved in GEMS, drawings updated and/or O&MMs updated (where applicable) by the agreed delivery plan and before DLP end. PAS PSS is to confirm this has been achieved. | It is expected that by HOTO, all Estate Data has been provided, validated for accuracy / completeness and GDL proved to PAS PSS. However there will be circumstances where items and/or defects will be identified during HOTO and DLP that require additional work or rectification. In these circumstances, the provision of remaining and/or corrected information to an agreed plan will occur. The contractor and PMCA / PM are to ensure and confirm to PAS PSS that all remaining and/or corrected estate data has been provided and saved in GEMS, drawings updated and/or O&MMs updated (where applicable) by the agreed delivery plan and before DLP end. PAS PSS is to confirm this has been achieved.